## tvrava Kale
4.6.3. | ESTIMATION OF THE ELECTRICAL INSTALLATION
Object: " at k.p. number 1435. K.O. Pirot - town
Each point of this scope includes the delivery of the main and the procurement and delivery of all auxiliary, necessary materials, i.e. all necessary works (and what is not explicitly stated) in order for the installation to be done in accordance with all standards and regulations and for it to function smoothly.
The offer includes insurance of the construction site (workers, bystanders, materials) with an authorized insurance company, as well as securing the construction site, workers and bystanders - by applying appropriate protective measures: fencing, signaling, etc.
During the warranty period, which is not shorter than 3 years, the Contractor is obliged to replace any part of the equipment that proves to be defective at his own expense, within the period determined by the Client. The warranty period begins on the day of connection to the power grid.
Payment will be made exclusively on the basis of the actually performed works (installed equipment and performed scope of works).
Описи у тачкама предмера имају приоритет у односу на текст дат техничким описом.
If "suitable equipment" is offered, the bidder is obliged to enter his offered type of equipment and manufacturer for all positions of the bill of quantities where this is requested. In that case, it is mandatory to attach a photocopy of the catalog representation of one or more elements that replace the equipment of the specified type, with all functional and technical characteristics. If nothing is entered, it is assumed that the already mentioned equipment is offered.
It is the bidder's obligation to enter the types of equipment offered and the manufacturer in places where the description does not specify the type and manufacturer. Here too, it is mandatory to attach a photocopy of the catalog representation of one or more elements that replace the required equipment.
All installed equipment must have the appropriate conformity document: declaration of conformity, test report, certificate, certificate of control.
Attestations, that is, certificates for lamps, which should be submitted with the offer are:
• ENEC certificate,
• Report on impact resistance testing (IK test) according to the EN 62262 standard,
•Mechanical protection test report (IP test) according to standard EN 60598-1,
• Report on the measurement of photometric characteristics according to the standards LM79-08, CIE 121-1996 and EN 13032-1, as well as certificates issued by the corresponding accredited laboratory according to the ISO 17025 standard, which prove the required photometric characteristics of the lamp,
• Report of the manufacturer of LED chips or LED lamps on the projected lifetime and maintenance of luminous flux according to LM80/TM21 standards, and
• Declaration of conformity with the CE mark, issued exclusively by the factory where the lamp is manufactured or assembled.
Attestations, certificates and reports can be submitted in Serbian and English.
If a lamp different from the reference lamp is offered, it is mandatory to submit a light technical calculation proving the fulfillment of the light technical conditions
поз. | DESCRIPTION | unit of measure | quantity
А | DECORATIVE LIGHTING OF THE NORTHERN AND SOUTHERN PARTS OF THE PARTITION WALL, GATE AND TOWERS I and II
1 | Main material
Luminaires are installed in everything according to the project and in a manner determined by the construction of the luminaire or by means of specified supporting accessories. The position of the lamps also includes a structure for hanging the lamps, which is solved on the spot. A brief description is provided for each lamp provided by the project. The power supply voltage of the lamps is 220-240V, 50Hz. The composition of the lamp includes light sources, and all auxiliary material for the operation of the lamp and their installation (holders, hangers, cables). The lamp manufacturer should operate in accordance with the quality management system ISO9001:2008, the environmental management system ISO 14001:2004 and the occupational health and safety management system ISO 45001:2018. All lamps in the offer should be from the same reputable manufacturer. All offered lamps should have the same or approximate characteristics and dimensions as the specified types of lamps.
1.1. | S1- Lamp for illuminating walls Linear surface-mounted light designed for lighting facades, with 36 high-efficiency LEDs. Total maximum power 100W and supply voltage of 220-240 VAC. The color of the light is RGB 3000K, with a color reproduction index CRI > 80. The optics of the lamp are C5, with a light emission angle of 15x55°. By moving the lamp closer to the surface to be illuminated, a more concentrated effect can be achieved. The lamp is controlled via a DMX controller. The durability of the LED source is 50,000 hours, provided that the luminous flux does not fall below 70% of the initial luminous flux of the lamp, L70B50. The housing of the lamp is made of extruded aluminum with cast aluminum ends, painted with electrostatic powder paint in dark gray color RAL7012. .
The optical block of the lamp is made of polymethyl methacrylate, while the protector of the lamp is made of thermally strengthened flat glass. The lamp supports are made of extruded aluminum, which have the possibility of adjusting the angle of inclination of the lamp along the horizontal axis in the range from +90° to -5°. The lamp's operating temperature range is from -40°C to +50°C. The overall dimensions of the lamp without the support are 1000 mm x 68 mm x 40.5 mm, while the dimensions of the lamp with the support are 1000 mm x 81 mm x 92.3 mm. The complete lamp has a degree of mechanical protection IP66. Impact resistance is IK06. Insulation class I. The lamp should comply with the European directives that apply to products, and have a CE mark.
| Lamp type UniStrip G5 BCP354 36LEDRGB30K220V C5L100 DMX 100W, manufacturer Signify, brand Philips or similar. | piece | 30
enter the type of equipment offered:
enter the name of the manufacturer:
1.2. | S2 - Luminaire for external lighting of towers Linear surface-mounted luminaire intended for lighting facades, with 36 high-efficiency LEDs. Total maximum power 100W and supply voltage of 220-240 VAC. The color of the light is RGB 3000K, with a color reproduction index CRI > 80. The optics of the lamp are with a light emission angle of 10°. The lamp is controlled via a DMX controller. The durability of the LED source is 50,000 hours, provided that the luminous flux does not fall below 70% of the initial luminous flux of the L70B50 lamp. The housing of the lamp is made of extruded aluminum with cast aluminum ends, painted with electrostatic powder paint in dark gray color RAL7012.
The optical block of the lamp is made of polymethyl methacrylate, while the protector of the lamp is made of thermally strengthened flat glass. The lamp supports are made of extruded aluminum, which have the possibility of adjusting the angle of inclination of the lamp along the horizontal axis in the range from +90° to -5°. The lamp's operating temperature range is from -40°C to +50°C. The dimensions of the lamp without the support are 1000 mm x 68 mm x 40.5 mm, while the dimensions of the lamp with the support are 1000 mm x 81 mm x 92.3 mm. The complete lamp has a degree of mechanical protection IP66. Impact resistance is IK06. The insulation class is I. The lamp should comply with the European directives that apply to products, and have a CE mark.
| Lamp type, UniStrip G5 BCP354 36LEDRGB30K220V 10L100 DMX100W, manufacturer Signify, brand Philips, or equivalent/COMPARABLE. | piece | 19
enter the type of equipment offered:
enter the name of the manufacturer:
1.3. | S3 - Gate lighting lamp Linear surface-mounted light intended for facade illumination, with 12 high-efficiency LEDs. Total maximum power 32W and supply voltage of 220-240 VAC. The color of the light is RGB 3000 K, with a color reproduction index CRI > 80. The optics of the lamp are with a light emission angle of 20°. The lamp is controlled via a DMX controller. The durability of the LED source is 50,000 hours, provided that the luminous flux does not fall below 70% of the initial luminous flux of the L70B50 lamp. The housing of the lamp is made of extruded aluminum with cast aluminum ends, painted with electrostatic powder paint in dark gray color RAL7012.
The optical block of the lamp is made of polymethyl methacrylate, while the protector of the lamp is made of thermally strengthened flat glass. The lamp supports are made of extruded aluminum, which have the possibility of adjusting the angle of inclination of the lamp along the horizontal axis in the range from +90° to -5°. The lamp's operating temperature range is from -40°C to +50°C. The overall dimensions of the lamp without the support are 300 mm x 68 mm x 40.5 mm, while the dimensions of the lamp with the support are 300 mm x 81 mm x 92.3 mm. The complete lamp is in the degree of mechanical protection IP 66. The impact resistance is IK 06. The insulation class is I. The lamp should comply with the European directives that apply to products, to have a CE mark.
| Lamp type UniStrip G5 BCP354 12LEDRGB30K220V 20L30 DMX32W, manufacturer Signify, brand Philips, or similar/Comparable . | piece | 4
enter the type of equipment offered:
enter the name of the manufacturer:
1.4. | Accessories, a set of 10 anti-glare shields for use with Uni Strip G5 lamps, made of steel and painted in dark gray. The protector should be resistant to atmospheric influences. The frame dimensions of the protector are 59 x 6 x 1000mm. Set of 10 protectors per package
| Philips ZCP354 L100 glare shield (10 pcs) or equivalent/comparable. | piece | 5
enter the type of equipment offered:
enter the name of the manufacturer:
1.5. | Accessories, a set of 10 anti-glare shields for use with UniStrip G5 lamps, made of steel and painted in dark gray. The protector should be resistant to atmospheric influences. The frame dimensions of the protector are 59 x 6 x 300 mm. Set of 10 protectors per package.
| Philips ZCP354 L 30 glare shield (10 pcs) or equivalent/comparable. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.6. | Accessories, a set of 10 pieces DMX "Lead" cable with 4 conductors, which must have a connector (termination) on one end that matches the specified fixtures, 2 meters long, to connect the fixture to the DMX control and wiring accessories. The cable is black.
| Cable type Philips ZXP399 Lead 4P DMX cable 2m (10 pcs) or similar. | piece | 2
enter the type of equipment offered:
enter the name of the manufacturer:
1.7. | Accessories, a set of 10 pieces DMX "jumper" cable with 4 conductors, which must have connectors (terminations) on both ends that match the specified fixtures, 2 meters long, to connect the fixture to the DMX control and additional wiring equipment. The cable is black.
| Cable type ZXP399 Jump 4P DMX cable 2m (10 pcs) or similar/comparable. | piece | 2
enter the type of equipment offered:
enter the name of the manufacturer:
1.8. | Accessories, a set of 10 pieces DMX "jumper" cable with 4 conductors, which must have connectors (terminations) at both ends that match the specified fixtures, 3 meters long, to connect the fixture to the DMX control and additional wiring equipment. The cable is black/comparable.
| Cable type Philips ZXP399 Jump 4P DMX cable 3m (10 pcs) or similar/comparable. | piece | 4
enter the type of equipment offered:
enter the name of the manufacturer:
1.9. | Accessories, a set of 10 pieces DMX "jumper" cable with 4 conductors, which must have connectors (terminations) at both ends that match the specified fixtures, 6 meters long, to connect the fixture to the DMX control and additional wiring equipment. The cable is black.
| Cable type Philips ZXP399 Jump 4P DMX cable 6m (10 pcs) or simila/comparable. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.10. | Accessories, a set of 20 pieces of DMX end connectors "female". The connectors are black.
| Controller type Philips ZXP399 endcap female connector (20 pcs) or similar/comparable. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.11. | Compact offline offline master DMX controller based on TCP/IP communication protocol, intended for small and medium lighting applications. Ability to control up to 700 DMX groups through scenes and animations located on the SD card. With the ability to amplify DMX signals in cascade connection, LCD screen and remote control. Input voltage is 12V DC, total power is 8W. The operating temperature range is from -30°C to +50°C. The frame dimensions of the device are 278 x 193 x 66 mm. Complete device in mechanical protection IP20. Insulation class III. The device has a mass of 1.55kg. The controller is black. The controller must comply with the European directives that apply to products, have a CE mark.
| Controller type Philips ZXP399 standalone controller 12V DMX or equivalent/comparable. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.12. | Sub-controller for DMX 512 control, based on TCP/IP protocol. With 8 output ports and support for automatic addressing. It is equipped with Art-Net support, two network ports for cascade connection and online firmware upgrade. Input voltage is 12V DC, total power is 13W. The operating temperature range is from -30°C to +50°C. The frame dimensions of the device are 277 x 193 x 66 mm. Complete device in mechanical protection IP20. Insulation class III. The device has a mass of 1.55 kg. The controller is black. The controller should comply with the European directives that apply to products, and have a CE mark.
| Controller type Philips ZXP399 sub-controller 12V 8 port DMX or equivalen/comparable. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.13. | Device for addressing DMX, input voltage from 6 to 24 VDC, frame dimensions 30 x 88 x 122 mm, complete device in mechanical protection IP20. The device is black. The device must comply with the European directives that apply to products, have a CE mark.
| Device type Philips ZXP399 Addressing Kit DMX or equivalent/comparable. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.14. | Signal amplifier, input voltage 12 to 24VDC, frame dimensions 25 x 40 x 136 mm, complete device in mechanical protection IP65. The device is black. The device must comply with the European directives that apply to products, have a CE mark.
| Device type Rhilips ZXP399 DMX/RDM amplifier 24V 4P or equivalent. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.15. | Power supply for amplifier or similar. | piece | 10
1.16. | 8-port Ethernet switch with four PoE ports for use with PoE-compatible controllers, input voltage from 100 to 240VAC, and maximum power of 63.2 W. Control via Ethernet IEEE standards include: 802.3 Ethernet, 802.3u, 802.3x Flow Control, 802.3 af. Housing made of aluminum painted black. The complete device is in mechanical protection IP20. The operating temperature range is from 0°C to +40°C. The frame dimensions of the device are 190 x 120 x 38 mm. The device must comply with the European directives that apply to products, have a CE mark.
| Device type ColorKinetics Power over Ethernet Switch 8-port gigabit switch, or equivalent/comparable. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.17. | S4 - Lamp for lighting the upper part of the gate. Projector for architectural outdoor lighting with 24 LED light sources with a maximum power of 50W. Neutral white light color temperature 4000K (Nominal). Multi-color light selection with red, green, blue and white light source colors (RGBW). Color uniformity SDCM = 4. Durability of the LED source is 50,000 hours L70. The minimum initial luminous flux of the lamp is 2,640lm, while the light efficiency of the lamp is at least 53 lm/W (Nominal). The ability to dim the light and select scenes and lighting colors via a power supply with a DMX interface. Power factor minimum 0.9. Operating temperature from -40°C to +50°C.
The housing of the lamp is made of aluminum alloy cast under pressure and painted with an electrostatic process, powder paint, while the cover of the optical part is also made of aluminum alloy cast under pressure and painted with an electrostatic process. The optical system is made of polymethyl methacrylate. The protector is made of thermally strengthened flat glass, and the seal is made of silicone. The complete lamp has a degree of mechanical protection IP66. Impact resistance IK08. Insulation class I. The lamp is designed to ensure easy recycling at the end of its working life, while all aluminum parts are identified for recycling. The lamp should comply with European directives that apply to products, to have a CE mark.
| Projector type UniFlood C BVP323 24LED RGBNW 220V 30 DMX or equivalent/comparable. | piece | 2
enter the type of equipment offered:
enter the name of the manufacturer:
1.18. | Accessories, a set of 10 pieces DMX "Lead" cable with 4 conductors, which must have a connector (termination) on one end that matches the specified fixtures, 2 meters long, to connect the fixture to the DMX control and wiring accessories. The cable is black.
| Cable type Philips ZXP399 Lead 4P DMX cable 2m (10 pcs) or similar. | piece | 2
enter the type of equipment offered:
enter the name of the manufacturer:
1.19. | Programming and commissioning of the lighting system | piece | 1
1.20. | Steel, round, conical pillars with a height of 5m. The post is made of steel in accordance with the standard SRP EN40 (1-9) for wind speeds in the area of ​​the fence according to the standard S 235 JR with invisible "plasma" welding dimensions: Column base Ø122 mm, without wings for reinforcement Column wall thickness 3.0mm The end of the column is flat for a lamp Ø60mm, length 85mm, and the column forms one unit without welding Anchor plate, square saucer-shaped with 4 elliptical holes for anchors, dimensions 271x271mm, thickness 4mm, and anchor spacing 200x200 mm according to the calculation of the column. Cast or tin cover for connection plate opening and fixing screw. Column cover dimensions 400x80mm. The lower point of the cover is 500mm from the anchor plate. Installation of the lamp directly on the top of the pole Column taper 1:12
Column equipment: Movable longitudinally movable support for connection plate, without connection box, One screw or grounding contact on the inside of the pole, Anchor basket according to the calculation of the column and anchor plate, minimum M18 200x200mm Caps for anchor protection, piece 4 AK pillar protection by hot galvanizing process in accordance with SRP EN ISO 1461, painted by electrostatic process in RAL color chosen by the Client. The pole is supplied with two rows of tapped threads for the lyre fixing screws at the top of the pole.
| Column type P 60 5.0 (3) 1:12 C SP 200x200 Zn PDG manufactured by Valmont or equivalent/comparable. | piece | 2
enter the type of equipment offered:
enter the name of the manufacturer:
1.21. | Connection box type RRS 12, material ASA+PC/ V-0, RAL 7035, manufacturer "EXTEH" or similar/comparable connection capacity of two cables 4x16mm2, Cu/Al, protection against contact IP 54, with a transparent cover above the automatic fuse. The box is equipped with a connection clamp made of polyamide PA 66 / V-0, RAL 9005 and a zeroing clamp, a DIN rail and an automatic fuse of 10A and/or 6A,1p, "C" characteristics, 10kA, in accordance with the standards EN 60493- 1, DIN VDE 0660-505, DIN 43628, DIN.43871. | piece | 2
enter the type of equipment offered:
enter the name of the manufacturer:
1.22. | Ribbed rubber pad measuring 260x260mm for leveling the column made of EPDM rubber. Rubber hardness 70±5 Shº, resistant to the influence of bases and acids, atmospheric influences and ozone aging and to temperatures from -25 to +120ºC. | piece | 2
enter the type of equipment offered:
enter the name of the manufacturer:
1.23. | Steel round lamp support 0.5m above the ground. The support is made of steel in accordance with standard SRP EN40 (1-9) for wind speeds in the area of ​​installation according to standard S 235 JR, dimensions in accordance with static calculation. AK support protection by hot galvanizing process in accordance with SRP EN ISO 1461, painted by electrostatic process in RAL color chosen by the Client. | piece | 53
1.24. | PP00-Y 4x1.5mm2 | m | 10
1.25. | P/F-Y 1x16mm2 | m | 2
1.26. | Cu rope 25mm2 | m | 2
1.27. | Tape 30x4mm SRPS N.B4.901Ч | m | 140
1.28. | Protective juvidur pipes fi 110mm | m | 140
1.15 | cable plastic protectors | m | 140
1.16 | warning bar | m | 140
1.17 | gravel | m3 | 5
1.18 | sand | m3 | 5
1.19 | concrete MB30 | m3 | 8
1.22 | okiten pipes f80 or comparable (for crossing purposes) | m | 15
1.23 | Supply pipes through the foundation for the entry of cables into the column through the foundation. Double "K" fork 60/60/45o+2xPVC pipe Φ110mm/60cm | piece | 2
1.29. | Cable markings | set | 1
1.30. | RO-JO - Distribution cabinet for public lighting Compact wardrobe with the following characteristics: - degree of protection IP55 in accordance with EN 60529; -guides on the upper side of the cabinet; - twice pickled 1.5 mm thick sheet, plasticized; -door opening up to an angle of 120°; - orientation dimensions 800x550x210mm; -type KB 2/5, manufactured by "Evrotehn", or equivalent/comparable. The wardrobe is equipped with:
Main disconnector, In=25A, 3p, 0-1, for DIN-rail mounting, equivalent to type VVD0, manufactured by Schneider Electric, 1 pc or COMPARABLE. - Distribution block, modular, for DIN-rail mounting, In=100A, 3p (or 4p), Ipk/60ms=10kA minimum, equivalent/COMPARABLE to type LGY410028, manufactured by Schneider Electric, 1 pc. -Miniature automatic switch, In=25A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74125, manufactured by Schneider Electric/OR COMPARABLE , 5 pcs. -Miniature automatic switch, In=16A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74116, manufactured by Schneider Electric OR COMPARABLE , 4 pcs. -Miniature automatic switch, In=10A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74110, manufactured by Schneider Electric/OR comparable , 5 pcs. -Power supply: 230Vac/12Vdc, equivalent to type ABLS1A12100, manufactured by Schneider Electric or comparable , 1 pc.
| Switch, equivalent /comparable to ColorKinetics Power over Ethernet Switch 8-port gigabit switch 1 pc. - DMX controller, 12V, equivalent/comparable to type ZXP399, manufactured by Philips, 1 pc. -DMX sub-controller, 12V, equivalent to type ZXP399, manufactured by Philips/or comparable, 1 pc. -Power supply: 230Vac/24Vdc, equivalent to type ABLS1A24100, manufactured by Schneider Electric, 1 pc. -DMX/RDM amplifier 24V, 4P, equivalent/comparable to type ZXP399, manufactured by Philips, 1 pc. - Complete set of installed, connected and marked equipment according to the cabinet scheme from the graphic documentation. On the lower side of the cabinet of the Pg cable entry, on the door of the cabinet prescribed markings: name of the cabinet, applied method of protection against electric shock. Place a pocket in the cabinet for documentation and the cabinet scheme, other necessary material for cabinet assembly and completion: DIN-rails, channels, conductors, sleeves, feet, row clamps, element labels, cabinet labels, laces, feet, other small material, necessary for planning, introduction and connection of input/output cables. | set | 1
enter the type of equipment offered:
enter the name of the manufacturer:
1.31. | Other unspecified material according to field needs: armature F16-22, row clamps, pertinax, plexiglass, cable lugs, screws, washers, graphite grease, etc. | complete | 1
Total main material:
2 | Works on the construction of decorative lighting
Note: All excavation work is done manually (no mechanical excavation) and under the supervision of an archaeologist, if no archaeological excavations have been done on that part, and all in agreement with supervision and a representative of the professional protection service.
2.1. | Geometrical marking of the route of the cable trench and the position of the poles (lamps) of external lighting. The protocol is submitted to the Investor on paper at the very beginning of the works. Calculation per length meter of the route of all cable trenches. Set with graphic and tabular specification of excavation areas (type, location and quantities). | m | 140
2.2. | Manual excavation of a trench 0.9 m deep in the green area, under the footpaths and parking lot, i.e. 1.4 m under the road; exceptionally in some places in agreement with the supervisory authority - depth as needed, in land of category III. Complete with backfilling and compaction in layers no thicker than 20 cm and obtaining a certificate of soil compaction (compaction in accordance with the purpose of the surface.) The trench is filled with sand under the footpath, parking lot and road. Note: All excavation work is done manually under the supervision of archaeologists, if no archaeological excavations have been done on that part, and all in agreement with supervision and a representative of the professional protection service. Calculation per meter of excavation. | m | 140
2.3. | Cable laying in the excavated trench freely and in plastic protective Juvidur pipes or comparble, fi 110 mm (offered price does not include excavation and backfilling). The method of laying the cable is as follows: in the trench in the green area above the cable, fine earth is poured in a layer 20 cm thick, and then earth from the excavation, plastic shields are laid 10 cm above the cables. At a depth of 0.4 cm from the level, a tape is laid to warn of the presence of the cable. A set with all the necessary bindings and auxiliary material. Calculation per long meter of laid cable. | m | 140
2.4. | Laying of galvanized steel strip 30x4 SRPS N.B.901 in a 0.1M thick bed of fine soil in an already excavated trench. A set with all the necessary bindings and auxiliary material. Calculation per long meter of tape. | m | 140
2.5. | Excavation of the foundation pit and backfilling around the foundation of the pillars. Note: All excavation work is done manually under the supervision of archaeologists, if no archaeological excavations have been done on that part, and all in agreement with supervision and a representative of the professional protection service.
Carry out processing of the foundation pit for the foundations of the columns. The processing includes: a) Excavation of a pit with a base at the bottom approx. 15 cm wider than the base of the foundation. The depth of the foundation pit is about 20 cm greater than the height of the foundation. The price includes the transport of excavated unused material to the landfill on the territory of the City.
b) Planing the bottom of the pit with an accuracy of ± 1cm and compacting the foundation subsoil by mechanical means to achieve the compressibility modulus Ms=25.0MN/m2;
c) Making a buffer under the foundation of the columns with a thickness of d=10cm from compacted concrete of compressibility modulus Ms=40.0MN/m2;
d) transportation from the workshop and assembly with foundation leveling
e) Backfilling around the foundation with compacted gravel of compressibility modulus Ms=25MN/m2; i.e. Ms=40MN/m2 layer 20cm below the pavement structure or 30cm below the soil with greenery.
. | Foundation pit for foundation dimensions 60x60x90 cm | piece | 2
| The foundation pit for the foundation measures 40x40x80 cm | piece | 53
2.6. | Production of concrete foundations for lighting poles according to given workshop drawings. The foundations of the columns are cube-shaped with given dimensions with one or two lugs for carrying them. The foundations were made in the workshop from non-reinforced concrete MB25 in smooth formwork, and in everything in accordance with the valid regulations and standards. Before concreting the foundation, place the supply plastic pipes D 110mm ("K" fork + 2x50cm pipes), anchor bolts that are delivered together with the columns and a central steel hook for transport. Anchors should be placed using "templates" so that the spatial geometry corresponds to the foundation (anchor) plates of the columns to be installed. The price of concrete, anchors and supply pipes are included in the position. Pillar foundations should be exceptionally worked upon approval of the on-site supervisory authority, only if the available space and surrounding installations require it. Calculation per piece of the derived, finished foundation. Kit with all the necessary material.
2.6.1. | foundation dimensions 60x60x90 cm | piece | 2
2.6.2. | foundation dimensions 40x40x80 cm | piece | 53
2.7. | Raising and installing a column of a given height on the foundation. Kit with application of pole markings in appropriate black paint and painting in two layers of the base of the pole with a special bituminous coating approx. 0.5 kg per pole. The anti-corrosion compound is ordered from the pillar supplier. Kit with templates, colors and all works, calculation per pillar.
2.7.1. | column 5 m high | piece | 2
2.7.2. | column 0.5 m above the ground | piece | 53
2.8. | Making the grounding of the pole, by connecting the grounding strap with the help of a T-U cross piece, cast in lead with a cut Cu rope 25mm2 with or without a crimped lug connected to the pole grounding screw (the other end of the rope). Kit with all necessary materials. Calculation by column position. | piece | 2
2.9. | lnstallation in the pole of the junction box with the help of galvanized sheet extensions and M10 screws. | piece | 2
2.10. | Zeroing, the neutral line on the junction box is connected to the earthing screw in the pole with a 16 mm2 Zhu-Ze conductor. If necessary, press a foot on the ends of the conductor. | piece | 2
2.11. | Production of cable terminations in the column. A set with the insertion of cables into the poles, the execution and labeling of all connections with nameplates. Calculation by column position. | piece | 2
2.12. | Installation of a lamp for outdoor lighting on a pole (console) 5m high. Kit with making the necessary connections. Calculation per lamp.. | piece | 2
2.13. | Installation of a lamp for outdoor lighting on a pole (console) with a height of 0.5 m. Kit with making the necessary connections. Calculation per lamp. | piece | 53
2.14. | Installation of the distribution cabinet PO-JO. A set with all necessary works, tests and commissioning. | piece | 1
2.15. | Breaking asphalt, concrete or behaton surfaces. After completion of the work, return to technically correct condition. The actual quantity will be determined on site.
2.15.1. | only breaking and cutting - asphalt | m2 | 1
2.15.2. | only breaking and cutting - concrete | m2 | 1
2.15.3. | only breaking - concrete | m2 | 1
2.15.4. | only breaking - dismantling - behaton | m2 | 1
2.15.5. | repair of asphalt surfaces | m2 | 1
2.15.6. | repair of concrete surfaces | m2 | 1
2.15.7. | repair of behaton surfaces | m2 | 1
2.16. | Installation of cable markings according to the project and the needs of the terrain. | set | 1
2.17. | Creation of the project of the derived state. (Only by written order). All changes that have occurred in relation to the main project should be entered into the project of the derived state. The project should contain a technical description of the performed works, both construction and electrical, the estimate and estimate according to the completed situation, the construction situation with precisely marked installed or existing SSROJO, power cables, poles and lamps, drawings of installed or existing all types of poles with consoles. The project is delivered bound in 3 copies and one on CD - in DOC, XLS and DWG format. | piece | 1
2.18. | Recording the route of laid cables, protective pipes and public lighting poles with the creation of a cadastre of the completed state. The recording is handed over to the investor at the end of the works - before creating the finished situation, in a paper and digital dorm on a CD in ACAD - "*.DWG" dormat (with a table of absolute coordinates of all poles as well as the breaking points of the cable route on the KAT-KOM substrates whose coordinate system is identical to the one on the bases owned by the City). This recording is the basis for the final calculation. Calculation per long meter of cable route. | m | 140
2.19. | Payment of mapping costs to the Republic Geodetic Institute. Calculation per meter of cable route. | m | 140
2.20. | Examination of cables, other conductors and connections in the installation. Obtaining verification reports from the competent institution, especially on the quality of insulation, protection against dangerous contact voltages, soil compaction, photometric measurements, internal technical acceptance, preparatory and final works. Trial operation and delivery of the object.
2.20.1 | Soil compaction certificates for all excavations depending on the purpose of the surface | lump sum | 1
2.20.2 | Electrotechnical certificates | lump sum | 1
2.21. | Costs of switching on and off at ED during the execution of works | lump sum | 1
2.22. | Preparatory and final works, test work and delivery of the object | set | 1
total construction works
RECAPITULATION
1 | MAIN MATERIAL
2 | CONSTRUCTION WORKS
А | TOTAL DECORATIVE LIGHTING OF THE PARTITION WALL, TOWER AND GATE:
Б | INTERNAL ELECTRICAL INSTALLATIONS OF TOWERS I AND TOWERS II
Each item of this scope includes the delivery of the main and the procurement and delivery of all auxiliary, necessary materials and all necessary work (and what is not explicitly stated) for the installation to function smoothly.
1. | Dismantling of the existing power installation. | set | 1
2. | S6 - Luminaire for internal functional lighting of towers Projector, surface-mounted luminaire, made in LED technology for mounting DALI three-phase rail, for accent lighting of the space. Dimensions of the projector length 187 mm, diameter fi 100 mm. The operating temperature range is from +10 to +40 degrees Celsius. The lamp is intended for frequent switching on/off. The lamp has a DALI driver in it, through which it is possible to control the lamp. Aluminum lamp housing, polycarbonate lamp reflector. The lamp and the support are white, RAL 9003. The degree of mechanical protection is IP20, IK02. Protection against electric shock is in class II. The lamp is supplied complete with LED modules with a light color of 3000K, ballasts and a color reproduction index of more than 80. Lamp efficiency minimum 125lm/W, total minimum flux of the system is 1800lm. The optic of the lamp is VWB (Very-Wide Beam). The maximum power of the lamp is 14.4W. Color uniformity, SDCM (0.38, 0.38) < 3. The durability of the LED source is 50,000 hours, with the fact that the flux does not drop to less than 70% of the initial one. The lamp should comply with the European directives that apply to products, and have a CE mark.
| Projector type Philips GreenSpace Accent Projecotr ST321T 17S/830 DIA-VLC VWB FG WH or equivalen/COMPARABLEt. | piece | 43
enter the type of equipment offered:
enter the name of the manufacturer:
3. | Accessories DALI three-phase white rail, length 1000mm, for mounting lamps type ST321T 17S/830 DIA-VLC VWB FG WH.
| Busbar type Philips RCS750 5C6 L1000 WH (XTSC6100-3) or equivalent. | piece | 7
enter the type of equipment offered:
enter the name of the manufacturer:
4. | Accessory, DALI three-phase white rail, length 2000mm, for mounting lamps type ST321T 17S/830 DIA-VLC VWB FG WH OR comparable.
| Busbar type Philips RCS750 5C6 L2000 WH (XTSC6200-3) or equivalent/comparable. | piece | 3
enter the type of equipment offered:
enter the name of the manufacturer:
5. | Main disconnector, In=25A, 3p, 0-1, for DIN-rail mounting, equivalent/COMPARABLE to type VVD0, manufactured by Schneider Electric, 1 pc. - Distribution block, modular, for DIN-rail mounting, In=100A, 3p (or 4p), Ipk/60ms=10kA minimum, equivalent to type LGY410028, manufactured by Schneider Electric, 1 pc. -Miniature automatic switch, In=25A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74125, manufactured by Schneider Electric, 5 pcs. -Miniature automatic switch, In=16A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74116, manufactured by Schneider Electric, 4 pcs. -Miniature automatic switch, In=10A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74110, manufactured by Schneider Electric, 5 pcs. -Power supply: 230Vac/12Vdc, equivalent to type ABLS1A12100, manufactured by Schneider Electric, 1 pc.
| Busbar type Philips RCS750 5C6 L3000 WH (XTSC6300-3) or equivalent/comparable. | piece | 6
enter the type of equipment offered:
enter the name of the manufacturer:
6. | Accessory, DALI three-phase white rail, length 4000mm, for mounting lamps type ST321T 17S/830 DIA-VLC VWB FG WH or comparable .
| Busbar type Philips RCS750 5C6 L4000 WH (XTSC6400-3) or equivalent/comparable. | piece | 6
enter the type of equipment offered:
enter the name of the manufacturer:
7. | Accessories, end cap for DALI three-phase rail, white color.
| Cover type Philips ZRS750 EP WH (XTS41-3) or equivalent/comparable. | piece | 22
enter the type of equipment offered:
enter the name of the manufacturer:
8. | Accessories, power supply for DALI three-phase rail, white color.
| Power supply type Philips ZCS750 5C6 EPSL WH (XTSC612-3) or equivalent/comparable. | piece | 22
enter the type of equipment offered:
enter the name of the manufacturer:
9. | Accessories, bracket for hanging mounting for DALI three-phase track, white color.
| Bracket type Philips ZRS700 SCP WH SUSP CLAMP (SKB12-3) or equivalent/comparable. | piece | 75
enter the type of equipment offered:
enter the name of the manufacturer:
10. | Installation of accessories and lamps for functional lighting. | set | 1
11. | S7 - Luminaire for illumination of decorative panels in the tower 2 Surface-mounted, external LED array of compact dimensions, intended for external application on architectural and media facades, bridges, arenas, theaters, amusement parks and recreation centers. The amount of light is 26lm, while the power is 1W, and the light efficiency is 26lm/W. The color of the light is in red, green, blue and white (RGBNW). The optical lens is made of transparent polycarbonate with a clear light distribution of 110° x 110° width. The input voltage is 24V DC, and the power factor is 0.9. The luminous flux tolerance is +/-10%. It supports dimmability with a maximum dimming level of 5%, and lighting control is achieved via the Dynamix DMX interface. The lamp has a 5-pole push-in connector for easier connection. The housing and optical cover are made of high-quality polycarbonate in an elegant black color. The overall dimensions are 43 x 16 x 38 mm, where the length is 38 mm, the width is 15.5 mm, and the height is 43.1 mm. The complete lamp is in mechanical protection IP66, while the impact resistance is IK06. The operating temperature range is from -40 to +50 °C. The lamp should comply with the European directives that apply to products, and have a CE mark
| Lamp type Philips UniString BWS300 4LED RGBWW 15V S DMX TM N16P12- 2m length or Comparable. | piece | 80
enter the type of equipment offered:
enter the name of the manufacturer
12. | Accessories, a set of 10 pieces DMX "Lead" cable with 5 conductors, which must have a connector (termination) on one end that matches the specified fixtures, 2 meters long, to connect the fixture to the DMX control and additional wiring equipment. The cable is black.
| Cable type Philips ZXP399 Lead 5P DC/DMX cable 2m (10 pcs) or similar. | piece | 8
enter the type of equipment offered:
enter the name of the manufacturer:
13. | Accessories, a set of 20 pieces of DMX end connectors "female". The connectors are black.
| Connector type Philips ZXP399 endcap female connector (20 pcs) or similar. | piece | 4
enter the type of equipment offered:
enter the name of the manufacturer:
14. | Accessories, mounting track or suitable. | m | 180
15. | Accessories, MeanWell 320W 15V outdoor driver or equivalent. | piece | 10
16. | Installation of lamps and accessories for lighting decorative panels | set | 1
17. | Programming and commissioning | set | 1
18. | Delivery of the necessary material and installation of the power supply of three-phase sockets 16A and fixed connection points, with cable type N2XH-J 5x2.5 mm2. The cable is laid on cable racks, through protective pipes and on the wall, under the plaster, in accordance with the architectural project. The cable must not be visible in both towers. In this regard, the cable is laid through protective pipes in tower 2, because it is being rebuilt, so it is possible to leave protective pipes through the walls that are being built, while in tower 1, which has existing walls, the cables are laid along the wall under the melter. The position includes the delivery and installation of a three-phase socket, making the power supply installation (on average 10m per connection point), with all the necessary materials and connecting the installation. | set | 1
19. | Delivery of the necessary material and installation of the power supply of single-phase 16A sockets and fixed connection points, with cable type N2XH-J 3x2.5 mm2. The cable is laid on the cable racks, through protective pipes and on the wall under the plaster, in accordance with the architectural project. The cable must not be visible in both towers. In this regard, the cable is laid through protective pipes in tower 2, because it is being rebuilt, so it is possible to leave protective pipes through the walls that are being built, while in tower 1, which has existing walls, the cables are laid along the wall under the melter. The position includes the delivery and installation of a single-phase socket, making the power supply installation (on average 10 m per connection point), with all the necessary materials and connecting the installation |  | 10
20. | Delivery of the necessary material and construction of the installation of the power supply of lighting points and fixed outlets, with cable type N2XH-J 3x1.5 mm2. The cable is laid on the cable racks, through protective pipes and on the wall under the plaster, in accordance with the architectural project. The cable must not be visible in both towers. In this regard, the cable is laid through protective pipes in tower 2, because it is being rebuilt, so it is possible to leave protective pipes through the walls that are being built, while in tower 1, which has existing walls, the cables are laid along the wall under the melter. The position includes the delivery and installation of switches, the construction of the installation of the power supply of lighting points, with all the necessary materials and connecting installations. | piece | 1
21. | RO-1 Supply, delivery and installation of a compact cabinet with the following characteristics: - degree of protection IP55 in accordance with EN 60529; -guides on the upper side of the cabinet; - twice pickled 1.5 mm thick sheet, plasticized; -door opening up to an angle of 120°; - orientation dimensions 800x550x210mm; -type KB 2/5, manufactured by Evrotehn", or equivalent. The wardrobe is equipped with:
Main disconnector, In=40A, 3p, 0-1, for DIN-rail mounting, equivalent to type VVD2, manufactured by Schneider Electric, 1 pc. - Distribution block, modular, for DIN-rail mounting, In=100A, 3p (or 4p), Ipk/60ms=10kA minimum, equivalent to type LGY410028, manufactured by Schneider Electric, 1 pc. -Miniature automatic switch, In=40A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74140, manufactured by Schneider Electric, 3 pcs. -Miniature automatic switch, In=16A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74116, manufactured by Schneider Electric, 8 pcs. -Miniature automatic switch, In=10A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74110, manufactured by Schneider Electric or comparable, 22 pcs. - DALI controller, 1 pc.
| A set of installed, connected and marked equipment according to the cabinet scheme from the graphic documentation. On the lower side of the cabinet of the Pg cable entry, on the door of the cabinet prescribed markings: name of the cabinet, applied method of protection against electric shock. Place a pocket in the cabinet for documentation and the cabinet scheme, other necessary material for cabinet assembly and completion: DIN-rails, channels, conductors, sleeves, feet, row clamps, element labels, cabinet labels, laces, feet, other small material, necessary for planning, introduction and connection of input/output cables, testing and commissioning | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
22. | RO-2 Supply, delivery and installation of a compact cabinet with the following characteristics: - degree of protection IP55 in accordance with EN 60529; -guides on the upper side of the cabinet; - twice pickled 1.5 mm thick sheet, plasticized; -door opening up to an angle of 120°; - orientation dimensions 800x550x210mm; - type KB 2/5, manufactured by "Evrotehn", or equivalent. The wardrobe is equipped with:
Main disconnector, In=40A, 3p, 0-1, for DIN-rail mounting, equivalent to type VVD2, manufactured by Schneider Electric, 1 pc. - Distribution block, modular, for DIN-rail mounting, In=100A, 3p (or 4p), Ipk/60ms=10kA minimum, equivalent to type LGY410028, manufactured by Schneider Electric, 1 pc. -Miniature automatic switch, In=40A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74140, manufactured by Schneider Electric, 3 pcs. -Miniature automatic switch, In=25A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74125, manufactured by Schneider Electric, 3 pcs. --Miniature automatic switch, In=16A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74116, manufactured by Schneider Electric, 11 pcs. -Miniature automatic switch, In=10A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74110, manufactured by Schneider Electricor comparable, 28 pcs. - DALI controller, 1 pc.
| A set of installed, connected and marked equipment according to the cabinet scheme from the graphic documentation. On the lower side of the cabinet of the Pg cable entry, on the door of the cabinet prescribed markings: name of the cabinet, applied method of protection against electric shock. Place a pocket in the cabinet for documentation and the cabinet scheme, other necessary material for cabinet assembly and completion: DIN-rails, channels, conductors, sleeves, feet, row clamps, element labels, cabinet labels, laces, feet, other small material, necessary for planning, introduction and connection of input/output cables, testing and commissioning. | piece | 1
enter the type of equipment offered:
enter the name of the manufacturer:
ELECTRICAL INSTALLATIONS TOWER I AND TOWER II TOTAL:
Ц | POWER CABLE LINES FROM OMM TO RO-1 and RO-2 TOWERS I AND II
Note: All excavation work is done manually (no mechanical excavation) and under the supervision of an archaeologist, if no archaeological excavations have been done on that part, and all in agreement with supervision and a representative of the professional protection service.
1. | Geometric marking of the route of the cable trench. The protocol is handed over to the Investor on paper at the very beginning of the work, and it can also be used to accurately determine the length of the cable due to the order. Calculation per length meter of the route of all cable trenches. Set with graphic and tabular specification of excavation areas (type, location and quantities). | m | 410
2. | Control manual excavation, so-called. "slicing", width 0.4m, length 2m, depth up to 1m, in order to accurately determine the position of the installations. | m | 3
3. | Manual excavation of a trench 0.9 m deep in the green area, under the footpaths and parking lot, i.e. 1.4 m under the road; exceptionally in some places in agreement with the Supervisory Authority - depth as needed, in land of category III. A set with backfilling and compaction in layers no thicker than 20 cm and obtaining a certificate of soil compaction (compaction in accordance with the purpose of the surface!). A trench is filled with sand under the footpath, parking lot and road. Calculation per meter of excavation. Note: All excavation work is done manually (no mechanical excavation) and under the supervision of an archaeologist, if no archaeological excavations have been done on that part, and all in agreement with supervision and a representative of the professional protection service.
| trench width 0.4m | m | 410
4. | Delivery and laying of galvanized steel strip FeZn 30x4mm, SRPS N.B4.901, in an already dug trench at a depth of 90cm, in a bed of fine earth 0.1m thick. Calculation per long meter of laid tape. | m | 410
5. | Delivery and laying of cable type PP00 A 4x25 mm2 in an already excavated cable trench. The cable is laid from the cabinet of the measuring point (OMM), next to TS "Kozaračka", to the distribution cabinet of Tower 1 (RO-1) and the distribution cabinet of Tower 2 (RO-2). The method of laying the cable is as follows: fine soil is poured over the cable in a layer 10 cm thick, then, if necessary, sand and crushed stone (under the road and parking lot), plastic shields are laid 10 cm above the cables. At a depth of 0.4 m from the elevation, a warning tape is laid. Kit with cutting, processing and marking the ends of the cable at the point of connection, as well as making the necessary connections. Under the road, parking lot and footpaths, the cable is laid through protective PVC pipe, fi 110 mm. Calculation per long meter of laid cable. The position includes the delivery of the necessary material and the connection of cables at both ends
| PP00 A 4x25mm2 | m | 800
6. | Delivery and installation of polyester measuring cabinet (OMM), for 2 measuring devices (IMO-2), made of polyester for external installation. The cabinet is placed against the outer wall of the TS "Kozaračka" substation, on a specially made concrete base. Kit with all necessary material . | piece | 1
7. | Breaking asphalt, concrete or concrete surfaces. After completion of the work, return to technically correct condition. The actual quantity will be determined on site.
7.1 | asphalt surfaces | m2 | 5
7.2 | concrete surfaces | m2 | 5
7.3 | betatonic surfaces | m2 | 5
8. | Drilling under the road or under the pipeline for laying PVC pipes fi 110mm. Kit with preparation, material and all works | m | 5
9. | Drafting of the finished state project (in accordance with the Law on Planning and Construction, by order of the Supervisory Authority. In the finished state project, all changes that have occurred in relation to the project for which the building permit was obtained should be entered. The project is delivered in 3 bound copies and one on CD in doc, xls and dwg format. | piece | 1
10. | During the laying of cables and PVC pipes (before backfilling the trench), recording the route of the laid cables, protective pipes with the creation of a cadastre of the completed state. The recording is submitted to the Republic and Geodetic Committee of the Mapping Institute and the investor. The recording is handed over to the investor at the end of the works - before the finished situation is created, in paper and digital form on a CD in acad - dwg format. This recording is the basis of the legal settlement. The recording is submitted to the Republic Geodetic Institute for mapping. A set with obtaining a confirmation of the submitted documentation to RGZ. Calculation per long meter of cable route. Calculation per meter of cable route | m | 410
11. | Payment of mapping costs to the Republic Geodetic Institute. Calculation per meter of cable route. | m | 410
12. | Outputs of the distribution or the organization that maintains public lighting on - off, during the complete performance of the works. Payment according to the attached invoice. | piece | 1
13. | During the excavation of the trench, loading the excavation directly into the truck or first into a cart and then into the truck. Set with removal and unloading to the city landfill (organization at the landfill is the responsibility of the contractor). Calculation per m3 of removed excavation. Before loading itself, the method is approved by the Supervisory Authority. | m3 | 10
14. | Delivery and installation of cable markings according to the situation and needs in the field. | set | 1
15. | Testing of cables. Obtaining verification reports from the competent institution,
15.1 | electrotechnical certificates | set | 1
CONSTRUCTION OF POWER SUPPLY CABLE LINES - TOTAL:
RECAPITULATION - ELECTRICAL INSTALLATIONS
А | DECORATIVE LIGHTING OF WALLS, GATE AND TOWERS:
Б | ELECTRICAL ENERGY INSTALLATIONS TOWER I AND TOWER II:
Ц | POWER CABLE LINES:
TOTAL (without VAT):
VAT:
ELECTRICAL INSTALLATIONS - TOTAL (with VAT):
Novi Sad, May 2024. Responsible designer:
Zorica Ninić Stupar, graduate electrical engineer