# VOLUME 3

# TECHNICAL SPECIFICATIONS

PROJECT OF ARCHITECTURE

CONSERVATION AND ARCHITECTURAL WORKS

TECHNICAL DESCRIPTION

The fortress is cultural property of exceptional importance and is under state protection. Accordingly, approval for Detailed design (PZI) for the execution of the works  has been obtained from the Institute for the Protection of Cultural Monuments in Niš, as the competent authority.

1. LOCATION

Pirot Fortress -Momchilo’s Fortress ("Kale") is a Serbian medieval fortification, categorized as a cultural monument of great importance and under state protection since February 16, 1953. year.
The area of the medieval fortress "Kale" with all its peculiarities and exceptional qualities, located in the wider city center, is one of the main resources that the city has at its disposal and on whose values it should plan further cultural and economic development.

The basis for the development of the Project is the Plan of Detailed Regulation "Kale" (hereinafter PDR "Kale") PDR "Kale" is an urban plan that elaborates in more detail the organization, construction and arrangement of the area included in the Plan with a special emphasis on its protection.

The project elaborates the urban planning unit P6 of the General Plan of Pirot with peripheral roads. The whole P6 belongs to the purpose of Public Greenery with guidelines from the GP that it is necessary to enrich it with commercial contents.
The protected area of the medieval fortress "Kale" is intersected by water bodies (Kostur river, Bistrica river, canal around the fortress) which impose a matrix of division and create 5 physically separate entities.
By analyzing the content, pedestrian traffic and defining the locations of future buildings, certain units were grouped into the following zones:

Zone A (park areas with the fortress)
  A1-triangular park area in the southeast of the whole
  A2-fortress complex covered by the canal (Lower, Middle and Upper Town)

Zone B
   B1-space between the bypass, the Bistrica river and the canal
   B2-triangular peninsula defined by the bypass, Bistrica River and Kostur River
   B3-space between the river Bistrica and Sarlach.

2. PARTITION WALL IN THE AREA OF THE LOWER CITY ZONE A2

This project envisages the reconstruction of tower I, tower II, as well as conservation and restoration works on the dividing rampart located in zone A2.
Tower I, tower II and the partition rampart are located on floor no. 1435 KO Pirot - a town owned by the City of Pirot.

The partition rampart  belong to an earlier phase of fortification and can be dated to the late 17th and early 18th century, when, after the defeat at Vienna, the Ottoman Empire entered a period of defensive military policy.

The northern part of the wall ends with a tower (Tower I), which is attached to the wall of the Middle Town. In the middle section of the wall is a gate, whose appearance is known from a drawing by S. Todorović from 1877.

The southern part of the wall also ends with a tower (Tower II), of which only one wall—the eastern one—is visible today. It was an open corner tower of an irregular quadrilateral shape, and a wall extended from it along the moat. The line of this wall, as well as part of the mentioned central tower within it, were visible in the early 1950s, at the height of the first row of loopholes or in the foundations. The remaining two walls of the corner tower (Tower II), which were visible up to a height of about 2 meters until the 1980s, have completely disappeared without a trace over the past twenty years.

The dividing wall (partition rampart ) and Towers I and II were built with two wall faces and an infill of rubble stone (“trpanac”). The wall thickness is approximately 1 meter. Three construction phases are clearly visible, especially on the eastern faces of the wall and towers. The oldest phase was built with lime mortar of a reddish color, and the wall faces were plastered. The younger phase was built with exposed joints, without plaster. The final phase represents the early 20th-century superstructure of the wall, constructed with only half the original thickness, as well as the blocking of the upper row of loopholes.

The corners of the towers were built from larger ashlars of travertine and sandstone.

The gate was constructed from cut sandstone blocks in its front section, including the door jambs, while the rear section was built using a combination of travertine ashlars and other types of stone. The door jambs feature profiled mouldings, and small niches are carved into the sandstone block.

Along the entire length of the wall and the towers, loopholes were constructed in two rows, measuring approximately 35 × 55 cm. The existence of an intermediate floor structure that enabled their use is evident. This is confirmed by square openings and remains of wooden beams in the tower and wall masonry. In Tower I and the northern section of the wall, these openings were sealed during previous conservation works, and are now visible only on the southern section. Here, on the interior face, the imprint of the beam support is also visible, positioned below the lower row of loopholes. In Tower I, the beam supports are still present below and above the upper row of loopholes, while in the lower level only their imprints remain in the masonry.

The project also includes archaeological investigations, which may provide the necessary data for the final definition of this fortification phase and its significant architectural elements.

The conceptual design for the reconstruction of the dividing wall and towers within the Pirot Fortress “Kale” (hereinafter: the Project) is based on the principle of cultural heritage revitalization within the framework of sustainable development. The introduction of new contemporary functions, appropriate to the monumental significance of the complex, is a prerequisite for successful revitalization adapted to modern needs, without endangering the authentic historical setting.

3. ANALYSIS OF THE CURRENT STATE OF THE PARTITION WALL AND THE PLANNED INTERVENTION
The Pirot fortress - Kale in today's spatial organization of the wider center is a city park and one of the favorite promenades of the residents of Pirot and guests of our city. The dominant place in the subject area is occupied by green park areas as the basic motif of the space.
In order to preserve the idyllic natural environment in the area of Lower Town, in the last 6 years, this area has been decorated, minimal paving has been done, which gives functionality to the area. Pedestrian access plateaus and walking paths are paved, green areas are arranged, and a children's playground is arranged. Paving was carried out with natural stone slabs of sandstone and split granite from the local area.

The partition rampart located in the area of the Lower Town (zone A2) is one of the most endangered parts of the fortress.

I Tower I - corner tower
II Tower II
III The northern part of the dividing rampart
IV Southern part of the partition rampart
V Gate
4 Newly designed plateau

Figure 3. Situational solution of the projected condition of the partition rampart of Lower Town

Figure 4. Eastern view of the dividing rampart of Lower Town, current state

Figure 5. Western view of the dividing rampart of Lower Town, current state

Various types of degradation have been observed on the partition wall and towers, therefore are planned conservation-restoration, research and rehabilitation works, as well as archaeological research.

Conservation and restoration works on the area of the partition rampart of the Lower Town will include the following:
• Partition rampart - its northern and southern parts;
• Tower I - with which the northern part of the dividing rampart ends, and which is attached to the rampart of the Middle Town;
• Tower II - with which the southern part of the dividing rampart ends, of which only one wall - the eastern one - is visible today;
• Entrance gate - located in the middle of the span of the partition wall - between the northern and southern parts of the partition wall;

After the preparatory works on the site (which aim to enable the unhindered execution of conservation-restoration and research works), different types of remedial works are approached, namely: static stabilization of the walls, rebuilding, building over the existing rampart walls, walls with two faces up to the elevation defined by the project, filling large openings with concrete and crushed stone and other conservation and restoration works.

Stone-cutting works are also planned: rehabilitation of existing floors made of stone slabs, coating of existing communications and the newly designed plateau with stone slabs, etc.

Carpentry works include: production and assembly of the roof structure of the gate, production of floors, staircases in the towers, production and assembly of wooden gate doors, etc.

Locksmith works include the manufacture and assembly of the steel mezzanine and roof structure in tower II and tower I, as well as the assembly of the glass facade that is connected to the supporting steel structure.

Archaeological research will foresee the placement of archaeological probes in the places determined by the archaeologist.

Hydrotechnical installations
It is necessary to create a water supply and sewerage project.

Electrical installations
Functional and aesthetic lighting is planned for both parts of the dividing rampart, both towers and gates, on the eastern and western sides of the rampart.
Create a project of electric power installations, based on the architectural foundations and according to the client's requirements.
The project envisages installations for the installation of new equipment in both towers.

Telecommunication installations
The project envisages the installation of telephone, internet and computer networks.
Video surveillance installations will not be the subject of the project.

Machine installations
Heating installation

It is necessary to provide heating in both towers, one that will be an exhibition space and the other that will become a cafe.
The project should respect the requirements of the competent institutions, first of all ZZSK Niš and the technical protection measures they will prescribe.

Installation of air conditioning
The project envisages an appropriate air conditioning system.
The building will also be treated in terms of fire protection with the necessary elaboration.

The planned function of the reconstructed parts of the ramparts and towers is primarily a performance space. Tower II will be given a new purpose and will become a cafe, on both levels, that will be used all year round. In the summer, the cafe's tables will be located on a plateau designed along the entire length of the partition wall on the western side.

4. REVITALIZATION OF THE PARTITION WALL OF THE LOWER TOWN

To this day, no part of the dividing rampart has been given an adequate modern purpose, so in the period that followed the last renovation, numerous damages occurred.
Based on the data obtained from the field research of the Institute for the Protection of Cultural Monuments from Niš and those available to them from previous research works, with the use of the available documentation provided to us, the project for the reconstruction of the ramparts, towers and gates of the partition wall of the lower town was started.
The basic idea was to determine the original forms through detailed analysis, to reconstruct them to the maximum extent with the correction of previous interventions, as well as to prepare both towers for modern use. As a result, they, as well as other fortification elements and the entrance gate itself, would be protected from further deterioration.

First, an ideal reconstruction of all the elements of the partition rampart was done. All available data were taken into account, and available photos and drawings were of crucial importance. The external appearance of the ramparts was not difficult to reconstruct, however, the internal elements were not visible on the old preserved documents, so analogies were used.

Figure 7. Ideal reconstruction of the partition rampart, towers and gate

In order to obtain a maximally functional space inside the towers and avoid the possible addition of parts that we cannot be completely sure are original in terms of form and materialization, after that it was proposed and agreed with the competent Institute for the Protection of Cultural Monuments to design a reconstruction, which was more reduced, while introducing modern materials. This reconstruction is further elaborated by the project.

Special attention was given to the reconstruction of the gate, where the preserved elements of the profiled decoration could be perfectly integrated with the appearance of the gate depicted in S. Todorović’s drawing.

As for tower I, the proposal for conservation and restoration works included the following tasks: the creation of a new modern mezzanine and roof structure (steel structure), a new roof covered with tiles, and a floor made of stone slabs.

For tower II, in addition to the already mentioned interventions (for tower I), it is planned to close with a modern glazed construction and cover with perforated panels, which would make this space usable for commercial purposes. For the perforation on the panels, a floral motif was taken from the ceiling of one of the Pirot houses (representatives of Old Varos architecture), which was built in the same period as the dividing rampart itself.

Both towers are given a modern purpose and their contents should contribute to the comprehensive revitalization of the Pirot Fortress.

5. NEWLY DESIGNED CONDITION - FUNCTION AND CONSTRUCTION


Tower I or corner tower

Tower I or the corner tower, of an irregular quadrangular shape, is located at the end of the northern part of the rampart. The stone walls with a thickness of about d=110 cm will be built up to the height provided by the project, with stone material that fully corresponds to the original material used for construction. And after that, the tower's roof, which currently does not exist, will be reconstructed. The corners of the tower are made of larger blocks of tufa and sandstone. Shotguns measuring 35 to 55 cm are located in two rows. The floor of the ground floor is designed from stone-sandstone slabs with a thickness of d=5-6 cm in cement mortar.

Given the lack of sufficient data on the appearance of the original wooden intermediate floor structure, the construction of a new intermediate floor structure made of contemporary materials is envisaged. The new system of columns and beams, as well as the staircase supports, will be made of steel. The intermediate floor structure and the staircase will be clad with high-quality timber. From the ground floor, a metal staircase with wooden treads will lead to the upper level.

The steel intermediate floor structure consists of metal columns and beams that will be physically detached from the walls of the towers in order to emphasize that this is an entirely new, contemporary structure that does not belong to the original construction period of the towers. Wooden planks with a thickness of d = 5 cm will be laid over the metal beams serving as floor joists. The roof structure is designed as a steel construction, while the roofing will be the authentic “ćeramida” tiles.

The loopholes will be adequately closed, and the entrance door will be made of high-quality wood.

The ultimate goal of this renovation will be to give the object a modern purpose, more precisely creation of an exhibition space in Tower I that will work throughout the year.


Tower II

Within the available dimensions, i.e. within the existing remains of the stone walls of tower II, the missing parts of the tower will be reconstructed. The reconstruction of two stone walls is planned, while the remaining two walls (which did not exist) facing the park will be given a modern outline in a combination of steel construction and glass.

The existing stone walls will be dismantled, as they are highly unstable. The new stone walls will rest on new reinforced-concrete foundations. Their stability will be enhanced with new reinforced-concrete tie beams and lintels, in full accordance with the structural calculations.

Reconstruction is to be carried out on the existing destabilized and deformed walls, which will first be taken down. The existing walls of Tower II will be completely rebuilt, ensuring that the corner stone blocks are returned to their original positions. The walls shall be rebuilt and stabilized up to their existing height, i.e., up to the height currently visible on site (ranging from 1.6 to a maximum of 2.6 meters). The new courses will be laid using the existing stone, following the original masonry pattern and regular bonding. The tower was originally built with a double-skin wall and a rubble-core infill (“trpanac”). The wall thickness is approximately 1.1 meters. The corners were constructed from larger dressed limestone (bigrа) and sandstone blocks. Larger stone pieces shall be installed at the corners, following the model of the existing structure. Upon completion, the masonry surfaces and joints shall be cleaned.

Reconstruction of both wall faces, thickness 20–30 cm

The rebuilding of both wall faces shall be carried out using existing stone and lime mortar, applying the traditional method and masonry technique. The mortar is based on natural hydraulic lime. It shall be prepared using RÖFIX NHL5, RÖFIX Belit fine mortar, and sand (0–4 mm) or equivalent materials. The volumetric mixing ratio is:

NHL 5 : Belit fine mortar : sand (0–4 mm) = 8 : 2 : 20.

The sand added on-site must comply with EN 13139 in terms of quality and grading curve.

If the existing stone is insufficient, rebuilding shall be completed with new stone of the same type and finish as the original.

Reconstruction of the rubble-core infill (“trpanac”), thickness 40–60 cm

The core infill shall be rebuilt using cement mortar, following the traditional method and masonry technique. When existing stone is insufficient, the work shall be completed using new crushed stone of the same type and finish as the original.

Note: During reconstruction, both wall faces must be built simultaneously up to a defined height, after which the space between them shall be filled, interlocking the stones from the wall faces with those in the core infill, and vice versa. Additional bonding shall be provided using anchors Ø 8 mm, length 50–60 cm, placed vertically every fifth course and horizontally at 3.5–4 m intervals, as shown in the drawings. Care must be taken to ensure that lime mortar (used for the wall faces) and cement mortar (used for the core infill) are not mixed during construction.

After masonry works are completed, joint finishing (dersovanje) shall be carried out. The exterior and interior faces of the walls, as well as the loophole openings of Tower II, shall be repointed using tinted lime mortar, following prior mechanical cleaning and washing of the joints. The cleaned external surfaces of the tower and the loophole openings shall be repointed with tinted lime mortar. The mortar shall be based on natural hydraulic lime and prepared using RÖFIX NHL5, RÖFIX Belit fine mortar, and sand (0–4 mm) or equivalent materials. The volumetric mixing ratio is:

NHL 5 : Belit fine mortar : sand (0–4 mm) = 8 : 2 : 20.

The sand added on site must meet EN 13139 requirements for quality and granulometric grading.

And these towers will get their new mezzanine construction, which will be made of modern materials.

The new primary steel structure consists of vertical columns and beams. The space between the pillars is closed with a high-performance aluminum lock. The secondary steel structure rests on the primary structure, the grill, on which the perforated panels are mounted. The panels are made of 5mm thick steel sheet, dimensions 200x100 cm and 100x100 cm. A certain number of panels are sliding, in order to provide visitors with sufficient comfort and quality of stay in the tower area. For the perforation on the panels, a floral motif was taken from the ceiling of one of the Pirot houses (representatives of Old Varos architecture), which was built in the same period as the dividing rampart itself.

Figure 12. Appearance of a perforated panel with dimensions of 100x100 cm

The tower II facility is closing and there will be a pastry shop that will be open all year round.
The floor of the ground floor is designed from stone-sandstone slabs with a thickness of d=5-6 cm in cement mortar. On the ground floor, a bar with a pantry was designed for the daily needs of the cafe-confectionery area. In agreement with the Institute, the toilet in this tower has not been designed, and visitors will have the opportunity to use a shared toilet in the immediate vicinity. A metal staircase leads to the first floor where there is an additional space.

In order for tower II to be able to accept the planned contents, it is necessary to introduce hydrotechnical installations and create a water supply and sewerage project.
It is also necessary to create a project for mechanical installations, heating installations, since it is necessary to provide heating in both towers, one that will be an exhibition space and the other that will become a cafe. The project will provide for an appropriate air conditioning system.
The buildings will be treated with the necessary elaboration in terms of fire protection.

Telecommunication installations
The project envisages the installation of telephone, internet and computer networks in the towers.

Video surveillance installations will not be the subject of the project.
The buildings will be treated with the necessary elaboration in terms of fire protection.

Electrical installations
Functional and aesthetic lighting is planned for both parts of the dividing rampart, both towers and gates, on the eastern and western sides of the rampart. It is necessary to create a project of electric power installations, based on the architectural foundations and according to the client's requirements. The project will foresee the installation of new equipment in both towers.

Special connections are foreseen, namely: tower II installed power 17.3 kW and tower I installed power 11.1 kW. The connections in both towers are three-phase. In both towers, a three-phase two-tariff meter and a permanent connection are planned. The number of measuring points is two.

Video surveillance installations will not be the subject of the project.

The northern part of the rampart

The northern part of the rampart, from tower I to the gate, will be built up to the height provided by the project, with stone material that fully corresponds to the original material with which it was built.

Stambol  Gate

Stambol gate will be built up to the height provided by the project. The masonry will be done in imitation of the existing ones: hewn sandstone blocks in the front part together with door frames, while the rear part is built in a combination of hewn tufa and other types of stone. It has molded borders on the jambs and small niches carved into the sandstone block. The gate is getting its own wooden roof structure, which will be covered with "tiles".

The southern part of the rampart

The southern part of the rampart, from the gate to tower II, will be built up to the height provided by the project, with stone material that fully corresponds to the original material with which it was built.

Newly designed plateau

On the western side of the dividing rampart, a plateau (marked with number 4 in Figure 3) was designed along the entire length of the rampart that is being reconstructed (from Tower I to Tower II). The newly designed plateau has the task of providing in the future sufficient comfort to all visitors to this area. Adequate furniture, tables and chairs will be found on the plateau, where visitors and citizens of Pirot will be able to refresh themselves and rest.

Materialization of the plateau

Materialization of the Plateau

It is planned to pave with natural stone slabs of sandstone and split granite from the local area.

Paving with natural stone slabs made of sandstone and split granite from the local area is planned. The stone will be laid on an appropriate base—a stabilized layer of gravel and sand—as follows:

Stone cubes (dimensions 8 × 8 cm, thickness 4–6 cm) – split brown granite (the visible top surface must be split and textured, while all other surfaces must be cut).

Stone slabs (dimensions 30 × 30 cm, 30 × 60 cm, 60 × 60 cm, thickness 4–6 cm) – Pirot split sandstone, dark brown (the visible top surface must be split and textured, while all other surfaces must be cut).

Stone slabs (width 30 cm, random length not less than 15 cm, thickness 4–6 cm) – Pirot split sandstone, dark brown (the visible top surface must be split and textured, while all other surfaces must be cut).

Between the newly designed plateau and the partition rampart, traditional “Turkish cobblestone” (kaldrma) will be installed—the historical paving material used during the construction period of the partition rampart. Its role is to emphasize the character and enhance the authenticity of the rampart, as well as to clearly separate the new from the old, the designed from the existing. The cobblestone paving will be executed in cement mortar, at locations indicated in the project. River cobbles will be set into a layer of cement mortar. The joints will be grouted with cement mortar, the joints shaped, and the stone cleaned.

The same type of stone will be used for paving in all zones (A2, B1, B2, and B3) within the project site.

The “four towers” motif, derived from the spatial organization of the medieval fortress itself, is used as the primary paving motif for the pedestrian plateaus.

Adequate physical and mechanical properties of the stone slabs are required: they must be resistant to wear, weather conditions (slipperiness, frost, and salt), and must have long durability and adequate compressive strength.

The slabs must meet the requirements of standard B.B3.200/94 for intensive pedestrian traffic, classification CX-02. As proof, a report from an accredited laboratory for testing according to SRPS standards must be submitted. The report must refer to the technical properties of the stone and its suitability for use as an architectural and construction material.

It is required that the slabs originate from the local area, as this type of stone was historically used as authentic building material within the protected cultural monument—the medieval fortress Kale.

Before commencing paving works, it is necessary to provide samples to the designer, the supervising authority, and the investor for approval.

NOTICE: “Should the technical description or any other part of the project documentation contain indications or references to a specific manufacturer, brand, or trademark of materials or products, the Tenderer  is free to propose an adequate and equivalent alternative from any other manufacturer. The project documentation does not favor any particular manufacturer of materials or equipment; such references are used solely for the purpose of defining the required items for the execution of works.”

CONSTRUCTION PROJECT

TECHNICAL DESCRIPTION WITH THE STRUCTURAL DESIGN
FACILITY: Partition rampart and towers in the area of the Lower Town of the fortress “Kale”
Storeys: Ground floor + 1
Plot No.: 1435 Cadastral Municipality Pirot – city
INVESTOR: City of Pirot

## STRUCTURAL SYSTEM OF THE FACILITY

### TECHNICAL DESCRIPTION OF THE STRUCTURE – TOWER 2

The structural analysis has been performed fully in accordance with EC2 regulations for concrete and steel structures. The analysis takes into account the self-weight of structural elements, live loads, and the effects of wind and snow. The structural calculations were carried out using the TOWER 8 software package and Excel files.

Tower 1 consists of a concrete and steel structural part, which together form a single structural unit.

The concrete part of the structure consists of the existing tower foundations and newly designed reinforced-concrete (RC) foundation beams 30/80 cm, into which the steel load-bearing columns are dowelled. It is necessary to carry out an expert assessment to determine the condition of the existing tower foundation supports, and if required, reinforce them by constructing RC  foundation pads. The dimensions and locations of all concrete structural elements are provided in the structural analysis and graphical documentation.

Connections between members of the steel structure are achieved by welding with 3 mm fillet welds. The steel structure is protected against corrosion with two coats of primer and two coats of finishing metal paint. Due to the configuration of the building, all lengths of steel members must be taken on site.

The steel structure consists of two independent systems.
The first system consists of members of the intermediate floor structure at ground-floor level. Steel columns made of HOP or comparable  100×100×4 mm are placed along the perimeter of the structure. At a height of 2.3 m, an intermediate floor structure is formed using HOP or comparable 140×80×4 mm  bars.The ground-floor area is accessed by a steel staircase made of two stringers 2×160×100×3.5 mm. Between the stringers, secondary beams made of L 40×40×3 mm are installed, with wooden treads placed over them. A steel ring beam made of HOP or comparable  100×40×4 mm is placed over the stone wall. The roof structure is formed using HOP or comparable 100×80×3 mm profiles, in accordance with the graphical documentation and structural analysis.

The second system consists of the steel roof structure supported on the perimeter walls. The dimensions of the steel structural elements are provided in the graphical documentation and structural analysis.

Loads from the roof structure are transferred onto the steel columns and the walls of the building, and subsequently to the foundations.

The connection between the steel columns and the foundation supports is made by welding onto steel base plates of 250×250×8 mm. These plates are anchored to the foundations with steel dowels or anchors 10 mm thick and 15 cm long. The dimensions and locations of all structural elements are provided in the graphical documentation and structural analysis.

For all concrete structural elements, the minimum concrete grade is MB25  ; reinforcement steel grades GA ( plain reinforcement steel) and RA ( ribbed reinforcement steel ) are used.
All steel structural elements are made of profiled steel in accordance with manufacturer's details.
The dimensions of all elements are provided in the structural analysis.

## TECHNICAL DESCRIPTION OF THE STRUCTURE – TOWER 1

### DESCRIPTION OF THE STRUCTURE

The structural analysis has been performed fully in accordance with EC2 regulations for concrete and steel structures. The analysis takes into account the self-weight of structural elements, live loads, and the effects of wind and snow. The structural calculations were carried out using the TOWER 8 software package and Excel files.

Tower 2 consists of a concrete and steel structural part, which together form a single structural unit.

The concrete part of the structure consists of reinforced-concrete strip foundations 110 cm wide and 40 cm high, above which dressed-stone masonry walls are constructed. At specific locations along the RC( reinforcement concrete ) strip foundations, RC ( reinforcement concrete )  columns are installed according to the design, interconnected with RC ( reinforcement concrete ) horizontal beams. In this way, a rigid load-bearing RC ( reinforcement concrete ) system is formed, capable of receiving loads from the stone wall. An RC( reinforcement concrete )  horizontal beam is also installed at the top of the stone wall. On parts of the façade walls, an RC( reinforcement concrete )  foundation strip 50×80 cm is installed, intended to carry the load from the steel load-bearing structure and façade cladding. Within the building, foundation supports are also installed to carry loads from the staircase and the steel load-bearing structure. The dimensions and layout of all concrete structural elements are provided in the structural analysis and graphical documentation.

Connections between steel members are achieved by welding with 3 mm fillet welds. The steel structure is protected against corrosion with two coats of primer and two coats of finishing metal paint. Due to the building’s shape, all lengths of steel members must be taken on site.

The steel structure consists of a system of steel members forming a single load-bearing structure. Steel columns made of HOP or comparable 110×110×4 mm are placed around the perimeter of the building. At a height of 2.3 m, an intermediate floor structure is formed using HOP or comparable 160×100×4 mm members. The ground-floor space is accessed via a steel staircase made of two stringers 2×160×100×3.5 mm. Secondary beams made of L 40×40×3 mm are installed between the stringers, with wooden treads placed over them. A steel ring beam made of HOP or comparable 100×40×4 mm is placed over the stone wall. The roof structure is formed using HOP or comparable 100×80×3 mm profiles, in accordance with the graphical documentation and structural analysis.

Loads from the roof structure are transferred onto the steel columns and the walls of the building, and subsequently to the foundations.

The connection between the steel columns and the foundation supports is made by welding onto steel base plates of 250×250×8 mm. These plates are anchored to the foundations with steel dowels or anchors 10 mm thick and 15 cm long. The dimensions and locations of all structural elements are provided in the graphical documentation and structural analysis.

For all concrete structural elements, the minimum concrete grade is MB25 ; reinforcement steel grades GA and RA are used -GA ( plain reinforcement steel) and RA ( ribbed reinforcement steel 
All structural elements are made of profiled steel in accordance with manufacturer's details.
The dimensions of all elements are provided in the structural analysis.

Responsible Designer

Branislav Kostić, B.Sc.Civ.Eng.

WATER SUPPLY AND HYDRAULIC INSTALLATIONS PROJECT

TECHNICAL DESCRIPTION

For the Detailed Design (PZI) of the RECONSTRUCTION OF THE PARTITION RAMPART AND TOWERS I & II IN THE LOWER TOWN AREA OF THE PIROT FORTRESS “KALE”, cadastral parcel 1435, Cadastral Municipality Pirot
Investor: City of Pirot, Srpskih Vladara St. 82, Pirot

I. GENERAL INFORMATION ABOUT THE STRUCTURE

The layout of the structure is shown on the attached site plan, including the method of connecting the water supply and hydrant network to the street water main Ø350 mm (for the café’s sanitary water and the external hydrant network of the fortress “Kale”), within a newly designed water-meter chamber as defined in the project.
The connection to the external hydrant network is made via an HDPE Ø110 mm pipeline in the connection manhole, while the café connection uses a PE Ø25 mm pipe.
The café’s sewer line is connected to the existing inspection manhole near the toilets by the Officer’s House, and is further connected via the existing sewer outlet to the municipal sewer in Vojvode Mišića Street.

The partition rampart and Towers I and II were built with two stone wall faces and an internal rubble-stone infill (“trpanac”), with an average wall thickness of about 1 m. Three construction phases are clearly visible, especially on the eastern faces of the rampart and towers.
The oldest phase was built using lime mortar with a reddish tint, with plastered wall surfaces.
The younger phase was built with visible joints, without plaster.
The final phase includes the rampart superstructure of half the original width from the early 20th century, and the closing of the upper row of loopholes.
The corners of the towers were constructed using larger carved blocks of tufa and sandstone.

The gate was built of carved sandstone blocks at the front section, including the door jambs, while the rear section was built using a mix of tufa blocks and other stone types. It features profiled borders on the jambs and small niches carved into the sandstone blocks.

Tower I

No works related to hydraulic installations are planned within this tower.

Tower II

Within the available footprint—i.e., within the existing remains of the stone walls—parts of the tower that are missing will be reconstructed. Two stone walls will be reconstructed, while the other two (which no longer exist) facing the park will receive a contemporary architectural treatment, combining steel structure and glass.
Tower II will be enclosed and will function as a small café–pastry shop operating year-round.
The ground floor flooring is designed as broken sandstone slabs, thickness 5–6 cm, laid in cement mortar. The ground floor includes a bar counter with storage space. In agreement with the Heritage Protection Institute, no toilet is planned inside the tower; visitors will use the shared toilet nearby, by the Officer’s House, completed in 2023.
A metal staircase leads to the upper floor with additional seating.

The gate (description repeated from above) was constructed from carved sandstone blocks at the front, with the rear section made of a mix of tufa blocks and other stone types, and includes profiled jamb borders and small niches carved in sandstone.

The PGD (Preliminary Design) for the reconstruction of the rampart and towers is based on the principle of heritage revitalization through sustainable development. Introducing new, contemporary functions compatible with the site’s cultural significance is a prerequisite for successful revitalization adapted to modern needs without compromising the authentic historical environment.

II. WATER SUPPLY

For the reconstruction of the rampart and towers, and due to fire protection requirements for a public-use facility, an external hydrant network is necessary.
The hydrant ring for the entire Lower Town area will be constructed in three phases:

- Phase 1: Implemented through this project (current PZI).

- Phase 2: Extension of the ring toward the Bistrica riverbed.

- Phase 3: Crossing over the Bistrica and final closure of the ring.

The water-meter chamber is constructed in Phase 1. It is shared between the external hydrant network and the café–pastry shop.
The chamber dimensions are 3.80 × 2.35 m, depth 1.70 m, built from reinforced concrete MB30, wall and slab thickness 20 cm. A cast-iron square cover 68 × 68 × 38 cm (SLR “Livac” Zrenjanin or comparable ) is installed in the corner.

The service line to the café runs from the water-meter chamber, which contains:

- DN100 mm Woltmann water meter – for measuring consumption of the hydrant network

- ¾" horizontal water meter – for the café

The water line to Tower II continues to the building via PE Ø25 mm pipes, transitioning inside the building to PP Ø20 mm pipes leading to the sink, below which a 10 L low-pressure compact water heater is installed.

The horizontal internal water pipeline slopes toward the vertical water riser at the building entrance.

The water supply pipes for Tower II and the hydrant network are laid in sand bedding, backfilled with gravel under paved surfaces, and with excavated soil in landscaped areas.

Phase 1 includes installing two underground hydrants DN80, one on each side of the rampart, as shown in the drawings. Underground hydrants are selected to avoid disturbing the visual integrity and authenticity of the fortress, which would be compromised by above-ground hydrants.

Upon completion of installation, pressure testing, flushing, and disinfection of the water supply and hydrant network are mandatory. A test report must be prepared and certified by the supervising engineer.

III. SANITARY SEWER SYSTEM

The internal sewage system consists of the sink drain and a floor drain beneath the bar counter.
The building includes one vertical drain Ø75 mm embedded into the wall near the sink, bending toward the façade wall, ending with an embedded cast-iron grille (recommended: cast-iron grate for tile stoves, SLR “Livac”, Zrenjanin or comparable).

The floor drain is 20 × 20 cm, cast iron, with Ø75 mm outlet, installed in the stone slab floor beneath the bar counter near the sink.

The sewer line leads to the newly designed inspection manhole No. 1 via PVC Ø100 mm pipes (1% slope). From Manhole No. 1, it continues through smooth PVC Ø160 mm SN4 pipes (for burial depth up to 4 m), slope 0.6%, to the existing inspection manhole near the public toilets.
The three inspection manholes are prefabricated units with conical tops and cast-iron frames with Ø52 cm covers.

Pipe bedding consists of sand with at least 10 cm of sand above the crown of the pipe. Backfilling is done with gravel on paved areas and excavated soil in landscaped areas.

Roof water drains freely onto the landscaped ground next to the building.

**TECHNICAL CONDITIONS

FOR THE EXECUTION OF WATER SUPPLY AND SEWER INSTALLATIONS**

1. Preliminary Measures

The water supply and sewer installations covered by this Project must be executed fully in accordance with the approved project documentation.

Before commencing the works, the contractor is obliged to inspect the site conditions in detail, determine the exact location of the water source, and properly construct the water intake with the catchment structure in accordance with technical standards. It is also necessary to compare the designed connection with the actual conditions on site and to consult the supervising authority regarding any ambiguities or potentially disputable issues.

Prior to implementing any modifications to the designed solution, the contractor must inform the supervising authority in due time and obtain the approval of the project designer.

2. Installation of Pipelines

The contractor is required to verify all elevation benchmarks specified in the project and compare them with the actual elevations on site. The pipeline installation must be carried out by qualified and trained personnel under the supervision of a competent professional.

For the sewerage system, the works must begin with the connection to the existing lower (main) sewerage network, after which the vertical stacks and branch lines may be installed.

All horizontal pipelines must be installed with the prescribed slope towards the lowest discharge point, in accordance with the applicable standards and project requirements.

4. The use of materials is permitted only if they comply with the relevant standards, and their condition must be checked on site before installation.

5. Only new materials and equipment may be used.

6. Galvanized pipes must not be bent, neither in a heated nor in a cold state; changes in direction and branching of the network must be performed using appropriate fittings.

7. Pipes passing through walls must run perpendicular to the wall surface; pipes may not pass diagonally through walls.

Notes on the storage and transport of PVC, PE, and PP water supply and sewer pipes:

Pipeline components must be transported in suitable vehicles and loaded/unloaded under professional supervision. During transport, pipes should, as much as possible, be supported along their entire length to prevent bending. Impact loads must be avoided, especially at temperatures below 0°C.

All pipeline elements must be stored so that their interior cannot become contaminated. When storing pipes, special care must be taken to prevent permanent deformation or damage. The storage stack height on site must not exceed 1.5 m. Pipes must be protected from contact with aggressive substances (e.g., solvents, wood impregnation agents). Pipes should be protected from sunlight and, where possible, covered. During loading, unloading, and transport, the pipes must not be dragged across the loading surface or the ground.

### PIPE PROTECTION:

- At locations where the pipeline intersects with other utilities, the pipes must be protected. When crossing with a sewer line, the water supply pipe must be positioned higher, and the space between them must be filled with compacted clay at a minimum thickness of 20 cm. If the distance is smaller, the water supply pipe must be placed inside a protective sleeve, as in the case of passing through a wall.

- In locations exposed to freezing, the pipes must be thermally insulated. The insulation must be installed carefully, and the pipelines must not be backfilled before the supervising authority inspects them.

- During work interruptions, the pipes must be temporarily sealed in an appropriate manner to prevent water contamination or filling with waste material.

### JOINTS:

- Joints between pipes and between pipes and fittings or couplings must be executed with utmost care. When connecting, the internal diameter of the pipe must not be reduced by any part of the fitting nor deformed by bending the pipe.

TECHNICAL REGULATIONS FOR SEWERAGE:

All wastewater and used water that can be easily rinsed away may be discharged into the sewerage system, provided they are sufficiently diluted by water to allow proper flow.

It is prohibited to discharge or insert into the sewer system any garbage, ash, rags, sand, kitchen waste, food scraps, ice, snow, bones, and generally all objects and materials. It is also prohibited to introduce flammable substances or those that may cause fire, explosion, or damage to the pipes and their functioning. Water and other liquids with a temperature higher than 35°C or containing harmful acids, alkalis, or salts may not be discharged into the sewer system.

Traps, toilets, and other facilities located below the backwater level of the street sewer may be connected to the property sewer only if the corresponding connection has automatic or manual backwater valves.

Dimensioning of the sewer network is carried out in accordance with applicable regulations and standards, whereby the flow velocity in horizontally laid sewer pipes must be between 0.6 and 3 m/s. The pipes must be buried at least 0.7 m below ground level.

In the direction of water flow, no transition from a larger to a smaller pipe diameter is allowed for any type of drain. Drains in one direction must not change gradient from a steeper to a less steep slope.

All horizontal sewer pipes that receive at least one toilet discharge must have a diameter equal to or greater than 150 mm.

Connection of horizontal sewage lines must be performed using fittings at an angle of 45° (Y-branch and bend).

The sanitary stack must have a diameter of 110 mm if at least one WC bowl is connected to it. In all other cases, the sanitary stack diameter is 75 mm. The design includes polypropylene sewer pipes. The sanitary stack must be located close to the WC bowl, at a distance not greater than 1.5 m.

Since the stack cannot be placed inside a wall, a dedicated installation shaft must be constructed for sanitary stacks.

The installation shaft, as well as the sewer stack, runs through the entire building (all floors) and must be positioned identically on all floor plans. The sewer network should be as short as possible and with minimal changes in direction.

### The drains from sanitary fixtures are defined in the table:

The pipes located in the horizontal plane of the upper distribution are installed with a slope of 1.5% toward the vertical stack.

| Sanitary fixture | Diameter of the sewer outlet pipe | Connection height on the wall |
| --- | --- | --- |
| Sink | Ø75 | 4 0 cm |
| Floor drain | Ø75 | — |

When sanitary stacks transition from the vertical section to the horizontal distribution at their lower end, their diameter must be increased as follows:

- from Ø75 to Ø110

- from Ø110 to Ø160

Revision shafts must allow maximum inspection and maintenance of horizontal sewer branches.

Concrete revision shafts are installed at street sewer connections. The spacing in a straight line must be a maximum of 160 to 200 pipe diameters. They are constructed using special concrete casting molds. The interior surface must be plastered with cement mortar and smoothed. The reinforced concrete slab above the shaft, as well as reinforcement layout, must correspond to the expected load. Shafts located in the groundwater zone must be protected against groundwater infiltration.

In all shafts where the joining or turning of drains is carried out using fittings, a bottom made of compacted concrete must be provided.

In all shafts with a depth greater than 80 cm, iron rungs (steps) must be installed with an alternating spacing of 30 cm. The first rung must be installed 40 cm below the cover.

## ANNEX ON OCCUPATIONAL SAFETY AND HEALTH

with an overview of occupational safety measures for the subject technical documentation, including all identified hazards and harmful effects that may occur during construction and use of the facility, and the prescribed measures for their elimination.

### 1. INTRODUCTION

- The company preparing the technical documentation must incorporate the prescribed occupational safety measures into the technical documentation and prepare a special annex on occupational safety, indicating all life-threatening hazards and health risks for workers and citizens that may occur during the use of the facility, as well as the measures foreseen for eliminating these hazards and reducing harmful effects to acceptable limits.

- The investor and the contractor must apply the prescribed occupational safety measures.

- The investor is obliged to notify the authority responsible for issuing the construction permit of the contractor’s name, the start date of construction works, and the planned completion date no later than eight days before the beginning of construction.

- The investor must submit, along with the request for issuing a construction or reconstruction permit, an opinion from an authorized occupational safety company confirming that the technical documentation and the occupational safety annex have been prepared in accordance with the occupational safety regulations, that worker safety in the facility has been ensured, and that the requirements of the technological-project brief for performing the technological process have been fulfilled.

- A contractor performing construction or reconstruction works on a building for longer than seven days is required to prepare a regulated Site Organization Study, which must be submitted along with the notice of commencement of works to the competent labor inspection no later than eight days before the start of work. The contractor must provide, maintain, and implement occupational safety measures on the construction site in accordance with the Site Organization Study.

- The authority responsible for issuing the construction permit for the investment facility must obtain the opinion of the labor inspection in advance.

- Before the start of construction, the investor is obliged to:

  - ensure the marking of the construction parcel, regulatory, leveling, and building lines in accordance with geodetic regulations;

  - ensure visible marking of the construction site with an appropriate signboard displaying information about the facility under construction, the responsible designer, the construction permit, the contractor, the start date, and the expected completion date.

- The commission for technical inspection of the completed or reconstructed facility is obliged, during the on-site inspection, to determine whether the prescribed occupational safety measures from the technical documentation have been implemented.

### 1.2. HAZARDS AND HARMFUL EFFECTS THAT MAY OCCUR DURING CONSTRUCTION

Hazards and harmful effects may occur during the construction of the sewerage network due to the following factors:

- execution of earthworks, carpentry works, loading–unloading, and installation works,

- insufficient training of workers employed at the site,

- improper selection of equipment, devices, and/or tools,

- improper handling of equipment, devices, and/or tools,

- failure to comply with applicable technical regulations and standards.

## 1.3. MEASURES FOR ELIMINATING HAZARDS AND HARMFUL EFFECTS DURING CONSTRUCTION

During the construction of the sewerage network, the following measures are foreseen to eliminate hazards and harmful effects:

- measures for protection and ensuring the safety of workers during the execution of works,

- other safety measures during the construction of the facility.

## 1.4. MEASURES FOR THE PROTECTION AND SAFETY OF WORKERS DURING THE EXECUTION OF WORKS

In accordance with the regulations in the field of occupational safety, the responsibility lies exclusively with the contractor, i.e., the person appointed by the official decision as responsible for the organization of construction – the site manager. The site manager, or another responsible person appointed by decision, is obliged to undertake and organize all measures necessary to ensure the safety of workers and the work process from accidents or damage, by applying the safety measures defined in the project, including shoring and securing trench walls with appropriate formwork, and issuing oral and written instructions to workers and foremen regarding conduct, movement, and procedures during the execution of works within the construction site zone.

Each worker is personally responsible for using personal protective equipment, depending on the nature and type of work performed.

The costs related to organizing and implementing worker safety measures during the construction works are borne by the contractor and are included in the unit prices of the works.

Failures in implementing safety measures during the execution of works constitute exclusive omissions by the contractor, including failures to comply with obligations arising from regulations on mandatory insurance of workers with the relevant insurance institutions (life insurance and

## 1.4.1. GENERAL NOTES AND OBLIGATIONS

- A worker has the right to working conditions that ensure his moral, psychological, and physical integrity and safety. A worker has the right to refuse work if there is an immediate danger to his life or health.

- Working conditions must be adapted to the physical and psychological characteristics and abilities of workers, and the technology and organization of work must be structured so that the worker performs tasks in an optimal position. The contractor is obliged to identify workplaces with special working conditions, if such workplaces exist.

- The contractor must consider the health condition of workers and their safety at work.

- The contractor is required to train workers for safe work on the construction site. Workers who have not received appropriate occupational safety instructions at their workplace must not be allowed to work.

- The contractor must provide workers with instructions for work along with the appropriate safety measures. For workplaces where there is an increased risk of injury or harmful effects on workers’ health, the instructions must be provided in written form.

- Workers entering employment for the first time must receive introductory occupational safety training, followed by on-site training at their workplace. Training in safe working methods and systematic instruction contribute significantly to preventing accidents and equipment failures during construction.

- Workers are obliged to immediately report to their direct supervisor any identified defects, malfunctions, or other occurrences that could endanger safety at work.

- The manufacturer of work equipment, installations, machinery, devices, and tools powered mechanically is obliged to provide instructions for use and safe operation, as well as a certificate confirming the implementation of safety measures and verifying that the equipment is safe to use.

- The documentation submitted together with the work equipment must also include data on their acoustic characteristics, showing that the noise level at workplaces and in work premises will not exceed the permitted values. If special measures (noise suppressors, elastic flooring, etc.) are required in order to meet the permitted noise level limits, these measures must be specifically indicated and explained in the said documentation.

- Work equipment, machinery, and other technical means must be installed and used in accordance with the manufacturer’s instructions and technical regulations, in a manner that ensures the appropriate safety of workers. Workers operating work equipment, machinery, or other technical means are required to use personal protective equipment whenever this is required by the manufacturer’s instructions and occupational safety regulations.

- The contractor is obliged to maintain work equipment in proper working condition and, during use and relocation to another work site, must inspect and verify its proper functioning.

- The contractor is obliged to apply occupational safety regulations to protect workers from noise at the construction site. Proper selection of construction machinery and vehicles must be ensured in order to acquire equipment with the lowest emission of noise and minimal vibration during operation. Furthermore, construction machinery and vehicles must be maintained in proper working condition throughout the execution of works to ensure maximum noise reduction.

- Hazardous materials that may cause occupational illnesses or injuries may only be used under conditions that ensure adequate worker safety and environmental protection. When no other adequate occupational safety measures can be applied, personal protective equipment must be used.

- Access to hazardous zones on the construction site is permitted only to workers who have received appropriate instructions and with the implementation of adequate safety measures.

- The contractor is obliged to warn every person present at the construction site, regardless of the basis on which they are there, about dangerous areas or potential health hazards, the protective measures they must apply, and to direct them to safe movement zones.

- The competent labor inspection authority shall file criminal and misdemeanor charges against responsible persons within the company if prescribed safety measures are not implemented, thereby endangering the health and life of workers.

1.4.2. SITE ARRANGEMENT, SAFETY, AND SECURITY

- Works must be executed in accordance with the technical documentation on the basis of which the construction permit was issued, and in compliance with applicable technical measures, regulations, norms, and standards for the construction of such facilities.

- The construction site must be organized in such a way as to allow unobstructed and safe execution of all works and to be secured against access by unauthorized persons.

- When several companies simultaneously perform works at the same site, each company is obliged to organize the work in a manner and with means that ensure the protection of all workers.

- The contractor is obliged to prepare a special study on the construction site arrangement, work organization, and occupational safety on the site, in accordance with legal regulations.

- The contractor is obliged to take appropriate measures, in accordance with the site arrangement and occupational safety plan, to ensure the protection of workers’ health and safety and to reduce risks in the work process such as mechanical injuries, electric shock hazards, hazardous substances, explosions, etc.

The contractor shall prepare a site arrangement plan containing the following elements:

• Securing the boundaries of the construction site in relation to the surroundings:
The construction site must be secured with fencing, covering the location of the working shaft, site facilities, auxiliary structures, storage areas for concrete elements, required materials and spare parts, as well as parking areas.

• Arrangement and maintenance of access roads

• Determining the type and placement of construction machinery and plants, with appropriate protection

• Location, space, and method for placing and storing construction materials:
Construction materials shall be stored at the working shaft area and at locations most suitable from the aspect of construction technology.

• Arrangement of electrical installations:
Electric power for operating motors, equipment, and lighting shall be supplied via cable from the nearest appropriate transformer station.
These works, including the installation of the metering unit, will be carried out by the competent Electricity Distribution Company. From the metering unit, electrical power will be distributed to consumers through appropriate cables and distribution cabinets.
The protection system is grounding (neutralizing). All electrical installations shall be executed in accordance with regulations. All distribution cabinets must be locked, with keys kept by the responsible and authorized electrician.

• Fire protection measures and equipment:
A fire may occur in construction site facilities (warehouse, dining area, etc.). To secure these premises, fire extinguishers type S-9 or S-12 must be installed.

• Method of transport, loading, unloading, and depositing various types of construction materials and heavy objects:
From the central warehouse, materials shall be transported to the installation site by trucks, with loading performed by cranes or manually.
Concrete is delivered by mixer trucks and installed using a concrete pump or by crane and concrete bucket.
Concrete preparation is performed in the central batching plant.
Excavation of soil shall be carried out either by mechanical screening or, in open excavation areas, by excavators with loading into trucks and transport to the disposal site.

• Work procedure in case of groundwater occurrence:
Groundwater intrusion shall be managed by pumping and discharging it onto free surfaces.

• Method of marking and securing dangerous places and zones on the construction site:
Hazardous areas may exist along the entire affected section.
Locations near the ground surface, as well as areas where inspection shafts, working shafts, or equipment extraction shafts are constructed, must be secured with fencing.
If the fence becomes unstable or damaged, workers must immediately inform the foreman or the site supervisor.

• Protection against falling from height or into depth:
Work on open excavations begins with excavation and securing trench walls with shoring.
In addition to personal protective equipment required for each workplace, workers must wear helmets while in the trench and during loading/unloading of construction materials.
Workers who are not trained in occupational safety cannot perform these tasks.
Personal protective equipment must be provided for all workers, and its use is mandatory.

• Organization of first aid and other worker protection measures:
First aid boxes shall be placed at the construction site.
The boxes must be supplied with all necessary materials.
If any material is used, it must be replenished immediately.

Boxes or first-aid cabinets must be locked, with the keys kept by the foreman or another responsible worker authorized by the foreman. One vehicle must be provided and always kept on the construction site. In case of a work-related injury, this vehicle shall transport the worker to the nearest medical facility. All workers must be trained in first aid during their occupational safety training.

The construction site must be fenced and properly marked.

Before the start of construction, preparatory works must be carried out, the site must be secured, and all works necessary to ensure the immediate surroundings, human life and health, and safe traffic flow must be executed.

To ensure safety when performing work in road-traffic conditions, and to prevent transport vehicles and cars from running into the work area or workers, the section of the road where work is being performed must be clearly marked with prescribed traffic signs and secured with protective barriers or other appropriate fencing and safety devices. At night and in conditions of poor visibility, the work area must also be marked with the required lights.

For protective fencing of work areas, appropriate traffic signs and a barrier painted alternately red and yellow in horizontal stripes 0.13 m wide must be used, with the top stripe being red.

After the protective fence is installed, the opening of the passable section of the road begins. Stone and broken pieces of asphalt or concrete must be placed behind the shields on the side facing vehicle traffic, creating a protective earth mound at least 0.5 m high and extending across the entire width of the excavation, to prevent vehicles from running into the workers.

The contractor must remove all traffic signs, barriers, and other devices installed during construction immediately after completing the work.

The contractor must prepare the following Instructions before starting the works on the construction site:

• Fire protection

• Safety measures during construction

• First-aid procedures

• Contents of the first-aid kit

• Instructions for operating the compressor station

• Jobs and work tasks with special working conditions

• Instructions for safe crane operation

• Safety measures for installing and maintaining temporary electrical installations

• Construction technology

Instructions referring to specific equipment, intended for its operation and maintenance, shall be displayed in a visible place so every worker can see them.

The persons responsible for implementing occupational safety measures on the construction site are the immediate supervisor, the construction foreman (for underground works), the site manager within their scope of duties, the machinery foreman of the work unit, and the machinery operations supervisor of the work unit.

Construction work may begin only when the site has been arranged in accordance with the provisions of the Regulation on Occupational Safety in Construction.

Before starting the works, the site must be cleared of all obstacles. Existing structures must be demolished, all trees cut down and sectioned, tree stumps removed, shrubs, small vegetation, and weeds cleared, and the material transported to a landfill approved by the competent utility services. The area must be completely cleared and topsoil removed.

The removed topsoil must be stockpiled aside in the surroundings, ensuring it is not mixed with other excavated material so it can later be reused for landscaping the site.

The required quantity of soil from the excavation to be used for backfilling shall be deposited within the construction site area, while any excess or unusable soil shall be transported to a landfill location jointly designated by the investor and the supervising authority.

1.4.3. SAFETY MEASURES AT WORK

The work process is carried out in an open area. The project includes the following types of works: earthworks, carpentry works, concrete works, and assembly works.

A. EARTHWORKS

The main causes of workplace injuries during earthworks include soil collapse into trenches and excavations due to insufficient shoring or lack thereof, as well as failure to maintain natural slope angles during excavation when shoring is not used.

In cities with heavy urban traffic, soil collapse is additionally triggered by ground vibrations caused by the movement of heavy transport vehicles. Therefore, earthworks involving trench preparation for sewer collectors must be performed in accordance with strictly defined technical conditions and shoring standards prescribed by the shoring design drawings.

Before excavation begins—and always after severe weather conditions, frost, or snow and ice melting—the excavation supervisor must inspect the site conditions and, if necessary, implement appropriate safety measures to prevent the collapse of trench sidewalls.

Manual excavation deeper than 1 meter must be performed under the supervision of a designated person. When the depth exceeds 1 meter, shoring must begin from ground level. Undercutting is strictly prohibited.

Shoring of trench sides is not required if the trench walls are sloped at the angle of internal soil friction (natural ground slope) for the soil category being excavated, nor during stepped excavation to depths less than 2 meters.

Shoring must be installed for vertical trench walls using 5 cm thick planks placed compactly or with spacing depending on soil category, positioned against the trench wall. Posts shall be braced with struts made of beams with a minimum diameter of 15–18 cm, secured with 5 cm thick planks.

The horizontal and vertical spacing of the struts shall be determined by specific drawings selected by the responsible site engineer.

Shored trenches and excavations located near previously backfilled depressions are hazardous due to possible soil collapse and must be placed under systematic supervision until the works are completed.

Removing shoring from trenches or excavations must be performed under technical supervision, as disassembly can cause soil collapse. Extra caution is required when removing shoring near building foundations or in unstable, slippery soil. In such cases, it is advisable to leave the shoring in place. When dismantling and removing shoring, the following safety precautions must be observed: before dismantling, all personnel must be cleared from the trench; shoring must be removed one strut height at a time, starting from the top and progressing upward as the trench is backfilled. The number of planks removed depends on soil compactness.

If installations are encountered during excavation, work must be stopped until supervision by a technical representative designated by agreement between the relevant utility organizations and the contractor is ensured.

If underground utilities (electric cables, pressure pipelines, gas pipelines, district heating lines, etc.) are discovered during excavation, continuation of work is permitted only using shovels without hard impacts. The use of tools such as picks, wedges, crowbars, etc., is prohibited to prevent accidents. Excavation must not proceed without representatives of the electricity utility, telecommunications company, waterworks, and gas company, in order to avoid damage to underground infrastructure and prevent accidents.

- For the descent of workers into the excavation and their exit from it, sturdy ladders must be provided, long enough to extend at least 75 cm above the edge of the excavation.

- For trenches deeper than 2 m, a solid barrier with a minimum height of 90 cm must be installed. For crossing over the trench, strong footbridges at least 0.8 m wide must be constructed, with firmly installed guardrails at least 1 m high and a toe-board at the bottom at least 20 cm high.

- During excavation or digging, a pathway at least 0.5 m wide must be left from the edge of the excavation. The pathway must be kept clean and, during winter, covered with sand.

- When excavated soil is being removed from a depth greater than 2 m, intermediate platforms with edge protection at least 20 cm high must be used. These platforms must be placed on special supports.

- Workers operating in wells and shafts must wear a safety belt with a retrieval rope and a signal rope for communication in case of danger.

To protect workers at the bottom of a well, shaft, or pit from falling material from the device used to remove excavated soil, a protective canopy must be installed at least 2 m above the bottom of the excavation.

If concrete or metal rings are used during the excavation of wells, shafts, or pits, the height of undercutting must not exceed 20 cm.

To prevent materials from falling into the well, shaft, or pit, a full protective barrier at least 1 m high must be installed around the edge. The wall of the well or pit may serve as a protective barrier, provided that it is continuously built up in case of any collapse.

Descending to or ascending from the bottom of a well, shaft, or pit using the material-lifting bucket is prohibited.

The winch used for lifting and lowering materials must comply with applicable safety regulations for crane operation.

- When operating a crane with a bucket, the condition of the rope lifting the bucket must be checked. Workers must not stand under a raised bucket.

- When excavating modern pavements, passages, and squares, as well as when installing collectors along main roads, the use of pneumatic tools powered by portable air compressors is recommended to facilitate workers’ efforts and speed up the work.

Work with pneumatic tools is permitted only for workers trained and specialized for such tasks and who have completed safety training.

To ensure safe working conditions, the valves on the handles of pneumatic tools must be properly adjusted, easy to open, and airtight when closed.

Hoses must be connected carefully to the air valve and the tool. Securing hoses with wire is prohibited, as poor connections can cause the hose to detach during operation and air pressure may injure the worker or nearby personnel.

The couplings used to connect hoses to pneumatic tools and air valves must have intact threads.

Air supply may be turned on only after the tool has been placed in the working position.

Repairing or adjusting pneumatic tools, or replacing their parts, during operation is prohibited.

To prevent flying particles of asphalt, concrete, or metal fragments (when striking pipes), workers operating pneumatic tools are required to use protective goggles.

When air leakage is detected, when a hose ruptures, or when work is interrupted, the air supply must be shut off by closing the valve on the air inlet.

Pneumatic tools must be regularly maintained and lubricated 2–3 times per shift with clean, low-viscosity oil. A new tool must be washed with petroleum after each shift, and after it has been run in, at least twice a week.

B. CARPENTRY WORKS

- Shoring must begin, as stated in the previous section, at depths greater than 1.0 m, starting from ground level.

- For shoring, a system of horizontal boards without gaps between them must be used.

- The formwork used to support the side walls of the trench must extend at least 20 cm above ground level to prevent soil or material from falling into the excavation.

- Fastening and securing elements for the shoring—such as wedges, frames, bolts, nails, wires, and similar—must comply with applicable standards.

- Removal of formwork must be carried out under the supervision of a qualified professional. If removing the formwork would endanger the safety of workers, the formwork must be left in the excavation.

C. LOADING–UNLOADING AND ASSEMBLY WORKS

- During loading–unloading and assembly operations, all applicable regulations and the instructions of the supervising authority must be followed.

- When leaving the garage, the truck driver is responsible for compliance with safety regulations. Workers must follow all safety-related instructions given by the driver during transport and while guiding the load to the worksite. It is forbidden for workers to sit on the sides of the truck bed, stand on the truck bed, or sit on the truck cabin roof while the vehicle is in motion.

- During transport, care must be taken to ensure that the load does not exceed the vehicle’s prescribed dimensional limits.

- Loading and unloading heavy pipes and other loads weighing more than 200 kg must be performed using a truck crane, tripods, pulleys, or winches. Particular attention must be paid to the strength of ropes (cables) and secure fastening of the load.

- For safe transport of materials, the condition of the surface over which the load is moved must be monitored. Such surfaces must not be slippery or contain unknown objects. In winter, slippery areas must be covered with sand.

- Rolling pipes from the unloading point to the installation point must be done manually and only with the use of crowbars and special metal or wooden pipe-rolling tools. Rolling a pipe toward oneself or standing in front of a moving pipe is prohibited.

- Pipes, prefabricated elements, and tools weighing over 80 kg must be lifted and lowered using a truck crane. If no crane is available, special pulleys mounted on a tripod or trestle must be used.

- If the load weighs less than 80 kg, lowering it into the trench may be done manually using a rope tested for double the load weight and free of splices or knots.

- Loads exceeding 80 kg may be lowered manually only when the volume of work is small, but in such cases no worker may bear more than 50 kg of load.

- When placing prefabricated elements into recesses, a secure support of short crossed planks must be positioned before releasing the slackened part of the crane rope.

- Installed pipes must be properly backfilled and compacted with soil.

- To avoid injuries when assembling flanged joints, alignment of openings must be checked using tools only, not by hand.

- During welding operations, workers must follow the specific instructions applicable to electric welders, gas welders, and their assistants.

- The worksite surface, as well as the trench or excavation where assembly is conducted, must be properly illuminated at night. For worksite lighting, electrical power of 120–220 V may be used, delivered through a special cable to the reflector, provided that the height of the installed lamp on the pole exceeds 2 m.

Use of electricity with a voltage not exceeding 24 V or lighting from portable battery-powered devices is permitted in excavations, trenches, shafts, large-diameter collectors, and damp rooms.
Voltage reduction must be performed using special portable transformers.

### 1.4.4. IMPROPER HANDLING OF EQUIPMENT AND TOOLS AND INSUFFICIENT TRAINING OF WORKERS

Improper handling of equipment and tools and insufficient training of workers refers to the human factor during work. To minimize these risks, it is necessary to:

- The manufacturer of mechanically powered work tools is obligated to provide instructions for safe operation and to certify on the tool itself that all safety measures and standards have been applied, or to supply a certificate of compliance with safety regulations together with the tool;

- The company must prepare regulatory documents in the field of occupational safety (Training program in occupational safety, Rulebook on inspection, testing, and maintenance of tools, devices and equipment, Program of safety measures and improvement of occupational safety, etc.);

- The company must not allow workers who are not qualified and trained in occupational safety to perform work tasks;

- The company is obligated to cooperate with inspectorates, report work activities on time, and request additional information and work permits.

### 1.4.5. PERSONAL PROTECTIVE EQUIPMENT

It is both the right and the obligation of workers to use personal protective equipment appropriately. Workers are required to immediately report any observed deficiencies to the directly responsible authorized person.

Workers must be provided with appropriate personal protective equipment (clothing and footwear) depending on the work tasks performed and the climatic conditions under which the work takes place.

For performing activities, depending on the type of facility, nature of the work, working conditions, risk of injury, exposure to dust or other harmful factors, personal protective equipment must be provided in accordance with the Rulebook on Personal Protective Means at Work and Personal Protective Equipment (Official Gazette of SFRY No. 35/69), including:

#### Protection of the head:

• Construction helmet.

#### Protection of the hands:

• Regular leather gloves;
• Leather gloves with lining for temperatures of –5°C and below;
• Leather gloves with steel rivets or plates;
• Gloves made of natural or synthetic rubber in various lengths.

#### Protection of the legs:

• Leather knee guards;
• Leather or heavy canvas shin guards with felt lining on the inside;
• Rubber boots.

#### Protection of the wrist and shoulder:

• Leather wrist guard;
• Leather shoulder guard.

#### Protection from moisture and cold:

• Raincoat made of rubberized or impregnated waterproof material for outdoor construction work;
• Rain hood or waterproof hat made of rubberized or impregnated material for protection of the head and neck from rain and wind.

Insulated clothing for protection against cold during winter work in outdoor spaces,
or in cold indoor areas;
• a fur coat or padded coat for protection against cold during outdoor work in winter. The coat
may be long or short;
• a mat made of leather or other insulating material.

- Eye and face protection against dust:
• eye and face shield against dust;
• eye shield;
• goggles with clear lenses and side protection;
• goggles with clear triplex glass and a sealed frame.

- Hearing protection during work with heavy machinery:
• earplugs for protection against noise levels of up to 105 dB.

- Respiratory protection against coarse, non-aggressive, and non-resistant dust:
• respirator for protection against dust and small quantities of harmful vapors;
• tube-type respirator.

- Fall protection:
• safety belts (with or without harness), with at least one “D” ring.

- Electrical protection:
• electrical insulating footwear;
• gloves made of electrical insulating material, as well as other equipment.

• All protective equipment specified here must, in terms of design and materials used, fully ensure protection from harmful external weather conditions.
• Workers who use protective equipment must maintain it in proper working condition. Damaged, torn, or worn-out equipment that cannot be repaired must be written off or destroyed.
• Equipment made of textiles or leather—such as protective clothing, footwear, and parts of footwear—must be regularly washed and cleaned depending on the material from which it is made.

### 1.4.6. FIRST AID

D. Contusions
For minor external contusions, it is best to apply a cold compress (sterile dressing).
In cases of severe contusions (including internal injuries), the injured person must be carefully placed on a stretcher, loosened from tight clothing, and emergency medical assistance must be called immediately. Until the arrival of a doctor or medical worker, cold compresses should be applied to the injured areas.

E. Sprains
In case of a sprain, the injured person should be positioned so that they feel no pain. A cold compress (sterile dressing) should be applied to the dislocated joint, and emergency medical assistance should be called.

F. Burns
Burns are caused by high temperatures or chemical substances. There are three degrees of burns:
• First-degree burns involve redness and a burning sensation;
• Second-degree burns involve blisters of varying sizes;
• In third-degree burns, tissue becomes charred and necrotic.

For first-degree burns, cold compresses (sodium solution) should be applied, or the area may be coated with petroleum jelly.
For second-degree burns, compresses should be applied around the undamaged skin surrounding the burn, or the area should be coated with clean petroleum jelly. Afterward, the injured person must be referred to a doctor.
Burn victims must not open blisters on their own.

To avoid tissue damage on an arm or leg during bandaging or when applying a tourniquet, something soft (handkerchief, sleeve) should be placed under the strap. After tightening, a sterile bandage must be applied to the wound, and the injured person should be immediately referred…

…the injured person to the nearest medical facility. It must not be forgotten that a tourniquet applied to an arm or leg must not be left in place longer than 1.5–2 hours, in order to avoid tissue necrosis. In cases of wounds, one must also remember that the wound may be contaminated with infectious microorganisms found on the object that caused the injury, as well as in dust, soil, or dirty dressing materials.
Special attention must be paid to wounds contaminated with soil in order to prevent tetanus infection (a severe disease with a high mortality rate). Immediate medical attention for the administration of a tetanus injection prevents this disease.

In order to avoid suppuration, the following rules must be strictly observed:

- the person providing first aid must carefully wash their hands with soap;

- the wound must not be rinsed with water or covered tightly;

- sand, soil, and similar debris must not be wiped from the wound (this may only be done by a physician);

- clotted blood must not be removed from the wound (as this may cause severe bleeding);

- the wound must not be bandaged with insulation tape.

### G. Fractures

In the case of fractures of the arm or leg, first aid consists of immobilizing the fractured limb.
Splints are used for immobilization. The splints are wrapped with cotton, placed along the fractured bone so that they cover the two joints nearest to the fracture (above and below), and then secured.

In the case of an open fracture, a sterile dressing must first be applied to the wound, and then the splint is secured.

Instead of a wooden splint, a board, ruler, piece of plywood, etc., may be used.
In cases of fractures of the femur or shinbone, and when a proper splint is not available, the injured limb is tied to the healthy one; in the case of arm fractures, the arm is tied to the torso.

For spinal fractures, the injured person must be placed on a wooden board or door and immediately transported to a medical facility.

### H. Assistance to a Drowning Victim

After removing the victim from the water, wet clothing must be removed, and the victim covered with a dry blanket or outer garment. The nostrils and mouth must be cleared of sand, mud, etc.
The victim should then be placed face-down over a bent knee, and by applying pressure between the shoulder blades, water should be expelled from the stomach and lungs. The victim’s head must be turned to the side.

After expelling the water, begin artificial respiration. Artificial respiration must be continued until the victim revives or until signs of death appear. At the first signs of recovery, the victim must be transported to a medical facility.

### I. Carrying and Transporting the Injured

When lifting, carrying, and transporting an injured person, no pain must be caused, nor should the victim be disturbed. Shaking, uncomfortable, or unsafe positions must be avoided.
The victim must be lifted and placed on the stretcher on command, and the victim is not to be lifted onto the stretcher; instead, the stretcher is slid beneath them.

On level ground, the injured person is carried feet first, and on a steep slope, head first.
The stretcher must be kept horizontal. To prevent rocking, the carriers must avoid stepping in alternating rhythm and lift their feet as little as possible while walking.

When carrying a severely injured person over a long distance, the stretcher is carried using straps attached to the handles and placed over the carriersʼ shoulders.

### 1.5. OTHER SAFETY MEASURES DURING CONSTRUCTION

Other safety measures during the construction period include the following:

- fire protection measures and equipment at the construction site

- measures for the protection, regulation, and safety of traffic in the street where the works are being carried out;

- measures for the protection and regulation of pedestrian traffic, as well as access to the yards along the construction front;

### 1.5.1. FIRE PROTECTION MEASURES AND EQUIPMENT AT THE CONSTRUCTION SITE

The entire fire protection system at the construction site shall be implemented in accordance with the Law on Fire Protection (Official Gazette of the RS, No. 111/09) and with the instructions of the supervising authority and the person responsible for fire protection in the company. All temporary structures must be secured.

Fires may occur on site accidentally or due to negligence. Fires in structures may occur primarily as a result of defects in the electrical network.

For fire protection, the following are provided: barrels of water, sand containers, and foam extinguishers, all with the necessary accessories. These items shall be placed next to the entrances of the temporary construction site structures made of solid materials and secured against fire.

Universal dry chemical extinguishers, type S-9, must be placed in visible and easily accessible locations, specifically:

- at the entrance door of room no. 1

- at the warehouse of room no. 1

In addition to procuring and properly installing the prescribed fire protection equipment, it is extremely important that all personnel on the construction site be trained in handling fire protection equipment so that they can use it immediately in case of need.

### 1.5.2. MEASURES FOR PROTECTION, REGULATION, AND SAFETY OF TRAFFIC IN THE STREET / ROAD WHERE WORKS ARE BEING PERFORMED

- The investor and the contractor are required to organize work on the public area or street in full accordance with the conditions and instructions issued by the competent authority for traffic organization, control, and safety.

- In this regard, the investor, together with the contractor, must prepare a Construction Organization Study, based on which the competent authority will prescribe conditions and deadlines for carrying out the works, establish a special traffic regime in the work zone, and define the requirements for arranging the construction site and traffic safety measures related to the works.

- Responsibility for any shortcomings related to traffic safety lies with the investor and/or the contractor.

### 1.5.3. MEASURES FOR PROTECTION, REGULATION, AND SAFETY OF PEDESTRIAN TRAFFIC AND ACCESS TO LOCATIONS ALONG THE CONSTRUCTION FRONT

- The Construction Organization Study must clearly define pedestrian routes and movement lines for passersby, with appropriate signs for information, warnings, and danger.

- Along these routes, suitable pedestrian crossings over trenches must be constructed, and fences, barriers, and protections must be installed in areas where the access of pedestrians and passersby is strictly prohibited (work zones, machine operating areas, crane operating areas, and areas of transport vehicles).

- The works may temporarily block or prevent access to yards and entrances to buildings for a maximum of 3 hours. If the scope or type of work requires blocking access for more than 3 hours, the investor, together with the contractor, must provide an alternative temporary access to the yard or building.

The sequence and dynamics of work progress must be organized by the contractor and investor so as to allow easy and rapid reopening of public areas for unobstructed pedestrian movement.

- Any shortcomings regarding the protection and regulation of pedestrian traffic, the movement of pedestrians and passersby, and access to yards along the construction front are the responsibility of the investor and/or the contractor.

### 1.6. CONCLUSION

- This report lists all the risks to which the workers involved in the construction of the subject facility, as well as those responsible for its maintenance and functional supervision, may be exposed. It also identifies and provides all necessary measures aimed at reducing the stated risks to the lowest possible level.

- The contractors and users of the facility must strictly adhere to all prescribed occupational safety measures, thereby preventing accidents and workplace injuries.

- By signing below, the responsible designer confirms that the project has identified and fulfilled all occupational safety measures prescribed by law/ In accordance with the measures and regulations pursuant to the Law on Safety and Health at Work of the Republic of Serbia

ELECTRICAL POWER INSTALATION PROJECT

## PROJECT SCOPE

This Electrical Installations Project covers the following installations:

- Functional and decorative lighting of the northern and southern sections of the partition wall, the gate, Tower I, and Tower II;

- Electrical power installations of Tower I and Tower II, in accordance with their planned purpose.

I – Tower I (corner tower)
II – Tower II
III – Northern section of the partition wall
IV – Southern section of the partition wall
V – Gate
4 – Newly designed plateau

Figure 3. Site plan – designed condition of the partition wall of the Lower Town

## DESIGNED CONDITION

### CONNECTION TO THE ELECTRIC POWER DISTRIBUTION SYSTEM

The connection of the facility to the electric power distribution system will be executed in accordance with the Design and Connection Conditions issued by EPS Elektrodistrbucija Srbije d.o.o., Belgrade, Elektrodistrbucija Pirot Branch, ROP-PIR-24313, No. 2540400-D-10.25-389350/2-23, dated 13.09.2023.

- Connection voltage: 0.4 kV

- Maximum power:

  - Business unit – Tower 1: 17.3 kW

  - Business unit – Tower 2: 17.3 kW

- Connection point of the facility: metering cabinet, downstream from the metering device

- Connection point to the system: existing low-voltage feeder in the 10/0.4 kV substation “Kozaračka”

The project specifies a standard polyester metering cabinet (OMM) for two metering devices (IMO-2), suitable for outdoor installation. The cabinet will be installed beside the exterior wall of the 10/0.4 kV “Kozaračka” substation, mounted on a specially constructed concrete base, in accordance with the Design and Connection Conditions of EPS Elektrodistrbucija Srbije.

From the metering cabinet to the distribution boards—separately for each business unit, Tower I and Tower II—the project specifies PP00 A type power cables of appropriate cross-section.
The route of the supply cable lines is provided in the graphical section of the documentation.

Power supply for the exterior lighting installation of the wall, gate, and towers is provided from a separate public lighting distribution board (RO-JO), which is powered from the distribution board of Tower 2 (RO-2).

## FUNCTIONAL AND DECORATIVE LIGHTING OF THE PARTITION WALL, GATE, TOWER I, AND TOWER II

The partition wall is divided into two sections: the northern and southern parts.
The northern part of the wall ends with Tower 1, which is attached to the wall of the Middle Town, while the southern part ends with Tower 2.

General illumination of the wall is designed using luminaires Uni Strip  G5 BCP354 36LED RGB 30K 220V C5L100 DMX 100W or comparable , with asymmetric optics, providing uniform wall illumination at a distance of 50 cm from the wall.

For illuminating the towers, Uni Strip G5 BCP354 36LED RGB 30K 220V 10L100 DMX 100W or comparable luminaires with narrow-beam optics are used, emphasizing the verticality and dominance of the towers relative to the wall.

Luminaires Uni Strip G5 for the exterior lighting of the towers, wall, and gate are mounted on steel brackets of appropriate height.

Special attention was given to the reconstruction of the gate, where the preserved elements of the profiled decoration could be perfectly integrated with the appearance of the gate as shown in the drawing by S. Todorović.

Using Uni Strip G5, BCP354 12LED RGB 30K 220V 20L30 DMX32W luminaires  or comparable with medium-beam optics, installed close to the façade at a distance of 20 cm, it is possible to highlight the profiled border on the doorjambs.

The Uni Strip G5 BCP354 36LED RGB 30K 220V C5L100 DMX 100W luminaires  or comparable are used to illuminate the niches in the gate entrance.

The lighting of the gate is designed as a combination of accent lighting and general illumination. Accent lighting highlights the profiled doorjambs, while the general illumination of the central upper part of the gate is provided by projectors mounted on poles.

Additionally, projections of the gate appearance, based on the drawings of S. Todorović, are planned to be displayed using LEKO LED luminaires equipped with GOBO glass. These projections would be used alternately with the general pole-mounted lighting, depending on the selected lighting scenario.

The complete lighting concept for the ramparts, towers, gate, and perforated panels is based on RGBW luminaires, which allow both standard white light and colored light options for ceremonial lighting scenes. Controllers and accompanying equipment are included in the delivery of the luminaires.

The project also includes the illumination of the perforated panels of Tower 2. The backlighting of the panels is designed with UniString BWS300 4LED RGBWW 15V S DMX TM N16P12 linear luminaires, or comparable  2 m in length, which are installed directly into the panels.

The panel manufacturer is required to provide adequate space and mounting brackets to integrate the luminaires within the panel structure. The installation method differs for movable and fixed panels. For movable panels, the cabling must be executed in a way that allows unobstructed movement of the panels while ensuring the proper and safe functioning of the lighting system.

Due to the transparency of the perforated floral pattern of the panels, this illumination will also be perceived as part of the decorative lighting of the façade of Tower 2.

The lighting solution for the perforated panels is designed with RGBW luminaires, which provide both white light and colored light options, depending on the requirements of ceremonial lighting scenarios. Controllers and accompanying equipment are supplied together with the luminaires.

The functional lighting of the interiors of Tower 1 and Tower 2 is designed with appropriate luminaires equipped with LED light sources, in accordance with the photometric requirements defined by the intended use and the architectural–structural project specifications.

The interior lighting of Tower 1 and Tower 2 is planned using GreenSpace Accent ST321 T 17S/830 DIA-VLC VWB FG WH track-mounted projectors. Surface-mounted tracks for the projectors are installed onto the load-bearing structure of the ground floor and onto the roof structure, following their dominant axes. The selected projector features a wide-beam optical system that provides uniform general illumination of the space. Track lighting is proposed to allow the luminaires to be oriented toward exhibition areas or supplemented with narrow-beam luminaires in case of modifications to the exhibition layout.

For the illumination of the ramparts, towers, and gate, ambient lighting luminaires equipped for LED light sources are specified, in accordance with contemporary lighting standards, while respecting criteria of functionality, energy efficiency, and economic feasibility of the installation. Luminaires with LED light sources emitting warm-white light (WW) with a color temperature of 2700–3300 K are adopted.

Luminaires for illuminating the walls, towers, and gate
A linear surface-mounted luminaire is specified for façade illumination, with a maximum power of 100 W and a supply voltage of 220–240 V AC. The light color is RGB, 3000 K, with a color rendering index CRI > 80. The luminaire optics are type C5, with a beam angle of 15×55°. The luminaires are operated via a DMX controller. The lifetime of the LED light source is 50,000 hours, with the requirement that the luminous flux does not fall below 70% of the initial output.

The luminaire brackets are made of extruded aluminum and allow adjustment of the luminaire’s tilt angle along the horizontal axis within a range from +90° to –5°.

Dimming capability, as well as selection of lighting scenes and color settings, is enabled through a power supply equipped with a DMX interface. The operating temperature range is from –40°C to +50°C. The luminaire has a mechanical protection rating of IP66, an impact resistance of IK08, and an insulation class of Class I. The luminaire is designed to ensure easy recycling at the end of its service life, with all aluminum components clearly identified for recycling. The luminaire must comply with applicable European product directives and bear the CE mark.

Poles
The luminaires for the decorative illumination of the gate are mounted on 5 m poles, positioned as shown in the site plan. In accordance with the SRPS EN 40 standard, steel poles with a height of 5 m are adopted. Corrosion protection of the poles must be carried out in accordance with domestic standards and ISO 1461 and ISO 14713.

The pole foundations are made of MB30 concrete, with dimensions appropriate to the structural requirements. Four anchor bolts and a double “K” fork, Ø110 mm, with extensions of the same diameter, are embedded into each foundation.

Cables
All earthworks for excavation must be performed manually (mechanical excavation is not permitted), under the supervision of an archaeologist in areas where archaeological excavations have not yet been conducted, and in coordination with the site supervisor and the competent heritage protection authority.

Cables are installed in a cable trench at a depth of 0.9 m below the ground level.
A galvanized FeZn 30×4 mm strip is laid parallel to the cable at a depth of 1.0 m for pole grounding. Crushed soil is placed over the grounding strip, after which the cable is installed and covered with an additional 0.2 m layer of crushed soil, followed by a GAL protective cover.

At a depth of 0.4 m, a warning plastic tape is installed, indicating the presence of buried electrical cables.

When laying cables parallel to or crossing underground infrastructure, minimum clearances defined by technical regulations must be observed.
At locations where the public lighting route crosses traffic surfaces, the cable is installed in PE conduits, Ø110 mm, at an appropriate depth in accordance with technical requirements.

The exterior lighting installation is executed using appropriate DMX cables for connecting the luminaires to the DMX control system. All equipment required for connecting the luminaires is supplied together with the luminaires.
The cable route for the public lighting installation and the layout of the luminaires are shown in the graphic section of the technical documentation.

Activation of the system is performed either manually or automatically via a time switch programmed with an astronomical clock – sunrise/sunset mode.

Applied protection system
The applied protection system against excessive touch voltage is the TN-C-S protection system. A FeZn 30×4 mm strip is installed as the protective conductor, laid parallel to the power cable. Accordingly, all conductive parts of the installation (poles, luminaires) that are normally not energized, but may become energized in case of a fault, must be bonded to the protective conductor connected to the public lighting grounding system.

### ELECTRICAL POWER INSTALLATIONS OF TOWER I AND TOWER II

Cables
In accordance with the SRPS N.B2.751 standard on selection and installation of electrical equipment based on external influences, the Regulation on Electrical Equipment Intended for Use within Certain Voltage Limits (Official Gazette RS No. 13/2010), and considering the concentration of people and more difficult evacuation conditions (BD2), the electrical installations are executed using halogen-free insulated cables with enhanced fire-performance characteristics.
Halogen-free cables do not release toxic combustion products in the event of a fire, limit fire propagation along cable routes, produce reduced smoke density, possess self-extinguishing properties, and maintain functionality during fire for 30 or 90 minutes (FE180/E30 or E90).

Cables with enhanced fire-performance characteristics must have Certificates of Conformity with IEC 60331, in accordance with Article 30 of the Fire Protection Law.

Fire-resistant cables with functional integrity during fire, such as type NHXHX FE180/90, must also have Certificates of Conformity with IEC 60331, in accordance with Article 30 of the Fire Protection Law (Official Gazette RS No. 111/2009, 20/2015).

Cable support systems and accessories used for routing fire-resistant cables must have Certificates of Conformity with DIN 4012, Part 12.

Penetrations of installations between fire compartments must be properly executed. At each penetration point, an appropriate fire-resistant sealing compound must be applied to protect the installation and seal the opening, ensuring that the fire resistance of the wall is maintained.
The fire resistance rating of the sealing compound must be equal to or greater than the required rating of the wall itself. Sealing must be performed at both entrance and exit points of the installation from the fire compartments, following the manufacturer’s instructions.

In both towers, cables must not be visible. Accordingly, in Tower 2, where the structure is being rebuilt, cables are routed through protective conduits embedded in newly constructed walls. In Tower 1, which has existing walls, cables are routed along the wall beneath the melter.

### Interior Lighting Installation

The building is equipped with both functional lighting and emergency, anti-panic lighting.

Functional lighting is designed using appropriate luminaires with LED light sources, in accordance with photometric requirements related to the intended use of each space and the specifications of the architectural and structural project. The protection level against external influences is selected based on the requirements of each individual room. The layout and types of luminaires are provided in the graphic section of the documentation.

The emergency lighting installation is designed with LED luminaires, ensuring safe evacuation along escape routes under fire conditions. Emergency luminaires are equipped with an independent power supply with a minimum autonomy of 80 minutes and switch on automatically in case of a mains power failure.

Emergency lighting luminaires must have certificates of conformity with the SRPS EN 60598-2-22 standard. Emergency lighting is designed in accordance with SRPS EN 1838 and SRPS EN 50172.

Activation of functional lighting is performed locally via installation switches.
The lighting installation is executed using N2XH-J installation cables of appropriate cross-section, according to the single-line diagram.

### Installation of General-Purpose Sockets and Fixed Consumers

For general-purpose and technological loads, the necessary number of single-phase and three-phase sockets with protective contact is provided, along with the required number of fixed connections. The number and layout of sockets and outlets are defined according to the purpose of the space, the arrangement of technological equipment, and coordinated with the other parts of the project documentation.

Power supply for sockets and fixed outlets is provided from the relevant distribution boards.
The installation of general-purpose sockets and technological consumers is executed using N2XH-J installation cables of appropriate cross-section.

### Protection Against Indirect Contact with Live Parts

Protection against electric shock, in accordance with SRPS N.B2.741, is achieved through protection against direct contact, protection against indirect contact, and equipotential bonding.
The applied protection system against excessive touch voltage is the TN-C-S system.

### Phased Construction

The construction of electrical power installations may be carried out in phases.

Responsible Designer:
Zorica Ninić Stupar, M.Sc.E.E.
License No.: 350 2661 03

### TECHNICAL REQUIREMENTS

#### . General Technical Requirements

- The technical requirements for the execution of electrical installations form an integral part of the project and are mandatory for the Contractor.

- The contract for the execution of works includes a specification of works according to which the works are to be performed.

- The contract for the execution of works is considered concluded when the parties have reached written agreement on all contract items and the price.

- The contract must contain:

  - the commencement and completion deadlines for the works;

  - the method of payment for completed works;

  - contractual penalties;

  - warranty period;

  - investor’s supervision of the execution of the facility;

  - the contractor’s obligation to perform the works in accordance with the approved project, as well as applicable standards, technical guidelines, and regulations.

- Upon taking over the work, the Contractor is obliged to inspect the construction site and verify the condition of civil works. Any deficiencies or remarks shall be reported to the Investor and agreed upon together with the supervising authority and the designer regarding the execution of the works or potential modifications. The works must not begin without the Construction Permit obtained by the Investor.

- Any elements not foreseen in the project documentation but required for the proper functioning of the installation must be reported by the Contractor in a timely manner to the Supervising Authority.

- The warranty period for the quality of installation works is the period defined in the Contract. The installed equipment is subject to the manufacturer’s warranty. If the acceptance procedure is not carried out on time at the Contractor’s request, the warranty period begins after the deadline by which the acceptance should have been completed, while the manufacturer’s warranty applies to the equipment. During the warranty period, the Contractor is obliged to remedy, at their own expense, all defects caused by poor workmanship or inadequate materials.

- The Contractor is responsible solely for the quality of installation works and installed materials if the works are performed according to the approved project or approved modifications. If the Contractor performs modifications without approval from the designer and the supervising authority, the Contractor bears responsibility for any malfunction of the installation.

- If the Contractor determines that, due to an error in the project or incorrect instructions by the Investor or the Supervising Authority, the works are being executed to the detriment of the durability, stability, functionality, or quality of the electrical installations, the Contractor is liable for the resulting damage if they fail to notify the Investor of the identified errors or incorrect instructions.

- All installed materials and equipment must comply with applicable technical regulations and standards. If the Supervising Authority requests testing of a material, the Contractor shall submit it to an accredited institution. If the material complies with the standards, the Contractor may charge the testing cost as additional work, along with the right to an extension of the deadline. If the material fails to meet the standards, the Contractor bears all costs without the right to compensation.

- If the Contractor installs materials provided by the Investor, the Contractor shall inspect them and, if considered inadequate, reject them in writing in the Construction Logbook. If the Supervising Authority nevertheless orders the installation of such material, the Contractor shall comply but shall not be responsible for the material or any consequences. In such a case, the warranty does not apply to this part of the installation.

- The Contractor shall be obliged to:

- carry out the works in accordance with the provisions of the project;

- execute the works in compliance with all applicable technical regulations, guidelines, and standards;

- take all necessary measures to ensure the safety of workers, passers-by, traffic, as well as the safety of the structure under construction and adjacent facilities;

- organize the work properly so as to cause minimal disruption to the activities of other companies or services.

13. If the Contractor determines that the installation works will not be completed within the agreed deadline, they must notify the Investor and provide an explanation for the delay.

14. The construction price of the electrical installation includes:

- complete installation, testing, and adjustment;

- training of the facility users immediately upon completion of installation;

- daily allowances and other compensations for installers and other personnel engaged in the works;

- performance of all required tests and trial operation.

15. If the Contractor notices that additional works not included in the contractual bill of quantities must be carried out, or if modifications arise that may affect the performance or scope of works, the Contractor is obliged to immediately submit a cost estimate for such additional works to the Investor. The Contractor shall commence such additional works or modifications only after the Investor approves the submitted cost estimate.

16. The Contractor must maintain a Construction Logbook and a Construction Diary in accordance with applicable regulations.

17. On the construction site, the Contractor is accountable solely to the Supervising Authority and communicates with it through the Construction Diary. Instructions issued by the Supervising Authority, whether by phone or in writing, become binding for the Contractor only after they are entered into the Diary. For all Contractor’s requests, the Supervising Authority must issue a decision within the contractual timeframe. Otherwise, the Contractor is entitled to a proportional extension of the deadline or compensation for damages due to delays.

18. The works specified in the technical specification shall be executed by the Contractor using an adequate number of qualified installers and assistant installers. The Contractor determines the required number of professional and auxiliary personnel at its own discretion, taking into account adherence to contractual deadlines.

19. For the certification of the Construction Diary, Logbook, and other official documentation, as well as for supervision of the works, the Investor must appoint a qualified person who will also represent the Investor in all matters related to the execution of the contracted works. The Investor must communicate the name of this person to the Contractor in writing.

20. All installations must be tested.

21. Minutes must be prepared for all performed tests and must contain:

- the subject of the test;

- a list of persons who carried out and attended the test;

- the date and time of the test, and the environmental conditions during testing (temperature, rain, etc.);

- the method of testing, including identification of the instruments and devices used;

- test results with recorded values, including a graphical representation if necessary;

- a conclusion stating whether the test meets the required criteria;

- handwritten signatures of the persons performing and witnessing the test.

22. The date of completion of installation works shall be considered the day when the Contractor submits a written report on the completion of the works to the Supervising Authority, and the Supervising Authority confirms this in writing in the Construction Diary or formally requests the Investor to appoint a Technical Acceptance Commission.

23. Before submitting the request to the competent authority for the execution of the technical inspection of the facility and obtaining the approval for commissioning, the user (investor) shall appoint qualified personnel who will carry out an internal technical inspection of the works performed in accordance with the project. A report shall be prepared on the internal technical inspection.

24. For the technical inspection, the contractor or investor is obliged to prepare the following documentation:

- the building permit for the facility, including the approvals of the competent institutions (telecommunications, water management, power supply, etc.);

- complete investment–technical documentation (mechanical, civil, electrical designs, workshop drawings) with all additions and modifications made during construction;

- the assessment of an authorized professional institution confirming that prescribed occupational safety measures and standards were applied during the design phase;

- the certification documentation of materials and equipment used during construction;

- records of performed testing of devices and the facility;

- the work log;

- data on the geodetic control of the executed route;

- reports on the internal technical inspection of the facility;

- manuals with installation diagrams required for commissioning.

25. The commission for the technical inspection of the facility is obliged to examine all the above-listed documentation as well as the fully executed facility. Upon completion of the review, the commission shall issue a professional opinion indicating whether the facility may be commissioned and under which conditions.

26. After obtaining the Use Permit from the competent authority, the facility may be put into operation.

27. These general conditions are mandatory for all participants in the construction process.

### 4.5.2.2. Technical Requirements for the Construction of Electrical Installations

1. The entire installation must comply with the regulations relating to electrical installations.

2. These technical requirements form an integral part of the project for the installation of the electrical system and are binding for the contractor.

3. All installations shall be executed entirely in accordance with the attached drawings, technical description, calculations, bill of quantities and cost estimate, these technical requirements, and the applicable technical regulations governing the execution of electrical installations.

4. During execution, the contractor must take into account all previously completed works on the building. If any completed works are unnecessarily or negligently damaged during electrical installation works, the contractor for the electrical installations shall bear the cost of the damage.

5. Prior to commencing the works, the contractor shall inspect the project on site, perform necessary corrections in cooperation with the supervising authority, and notify the investor of any deficiencies, required additions, or modifications. For all deviations from the project, the actual quantity of materials and labor shall be charged. Major changes require approval from the designer or the commission inspecting the facility.

6. Drilling into steel–reinforced concrete columns is not permitted without the approval of the supervising authority.

7. When installing cables or conductors in conduits, all conductors belonging to the same circuit must be placed within the same conduit or cable.

8. The connection of conductors may only be made in junction boxes, switchboards, or manholes.

9. Metal protective coverings of pipes and cables must not be used as a protective conductor or as an earthing conductor.

10. Conductors belonging to different electrical circuits may be installed within the same junction box or manholes.

11. Switches or fuses shall be installed only on phase conductors.

12. Bends in conduit routes must be executed so that no irregularities remain along the cable path.

13. Switches and sockets shall be recessed into boxes, and all of their parts that are normally not live must be made of insulating material.

14. Neutral conductors must not be fused and must be distinguishable by color from phase conductors. In both electrical and mechanical terms, conductors must form a continuous whole.

15. The neutral conductor must be light blue in color.

16. The PE conductor must be yellow–green.

17. All metal parts of electrical installation devices (distribution boards, luminaires, etc.) must be protected against hazardous touch voltage.

18. Work on electrical devices must be carried out only when the system is de-energized.

19. The de-energized condition must be ensured by the operator of the electrical system on which the works are being performed, in the presence of a representative of the contractor.

20. Re-energizing of the system must be performed by the operator of the electrical system on which the works are being carried out, in the presence of a representative of the contractor.

21. All materials to be installed must be of first-class quality and manufactured in accordance with applicable standards.

22. Low-current conductors must be placed in separate conduits.

23. The insulation resistance between conductors and with respect to earth must be at least 500,000 Ω (according to the Technical Regulations for Low-Voltage Electrical Installations), and this must be verified by measurement. This applies only to strong current installations, i.e., 220 VAC systems.

24. The supply of complete materials, transportation, all installation, assembly, masonry, painting, and other works connected to the execution of the installation shall be borne by the contractor.

25. The contractor guarantees the correctness of the executed works in accordance with the conditions of the Contract.

26. Before starting the works, the contractor must inspect the project on site, make necessary corrections in cooperation with the supervising authority, and inform the investor of any deficiencies, required additions, or alterations. For all deviations from the project, the actual cost of materials and labor shall be charged. Major changes require approval from the designer or the commission inspecting the facility.

27. After trial commissioning, the contractor shall ensure that all required testing of the new public lighting installation is performed, in accordance with the Technical Regulations for Low-Voltage Electrical Installations and applicable standards, by a company authorized to perform such testing.

28. The type of distribution system and protection system shall comply with SRPS HD 60364.

29. Upon delivery of equipment and materials to the construction site, the supervising authority must inspect them and verify their condition. All installed materials and equipment must be of first-class quality and supplied with certificates and declarations of conformity.

30. The first energizing of equipment shall be carried out in the presence of the Equipment Supplier’s representative (if the equipment is specific to that extent), the Contractor, and the Supervising Authority. The Contractor shall not be responsible for failures resulting from improper operation.

31. Upon completion of all works, testing of all installations must be carried out in accordance with the applicable regulations. The obtained results must fall within the limits prescribed by the regulations. If the installation is found to be defective during testing, the Contractor is obliged to bring it into proper working condition at their own expense.
The takeover of the installation from the Contractor may be carried out only after all works have been completed and the installation has passed all required performance tests.

32. The Contractor is obliged to prepare and submit to the supervising authority and the investor the as-built design documentation.

ANNEX – OCCUPATIONAL SAFETY MEASURES

This Annex has been prepared in accordance with Article 7 of the Law on Safety and Health at Work (“Official Gazette of the Republic of Serbia”, No. 101/05 of 21.11.2005 and 91/2015).
A preventive safety measure consists of informing the personnel about the hazards to which they may be exposed and implementing appropriate protective measures (protective equipment, procedures) against such hazards. Personnel must be trained in providing first aid, and first-aid equipment must always remain complete and available to the working team, together with other protective equipment.

Locations Where Hazards and Harmful Effects May Occur

- Control switchboards

- Electrical installations

- Areas in the vicinity of lightning protection conductors during severe storms

### Hazards and Harmful Effects That May Occur During the Use of Electrical Installations and Equipment

- Direct electric shock

- Short-circuit currents

- Excessive touch voltage

- Accidental contact with live parts

- Overloading

- Unacceptable voltage drop

- Mechanical damage

- Exposure to moisture, water, and dust

- Atmospheric discharge

### Prescribed Measures for Eliminating Hazards and Harmful Effects

- Protection against direct electric shock is ensured by selecting equipment and components manufactured by registered producers, in accordance with applicable standards. The equipment and components are installed in switchboards equipped with locks and keys, and marked with warning signs.

- Protection against short-circuit currents is provided through proper selection and dimensioning of automatic circuit breakers in accordance with the Rulebook on Technical Normatives for Low-Voltage Electrical Installations (Official Gazette of SFRY No. 53/88, Official Gazette of FRY No. 28/95).

- Protection against excessive touch voltage is achieved through automatic disconnection of supply in a TN network system, as prescribed by SRPS IEC 60364-5-51:2008.

- Protection against accidental contact with live parts is ensured in accordance with the Rulebook on Technical Normatives for Low-Voltage Electrical Installations (Official Gazette of SFRY No. 53/88, Official Gazette of FRY No. 28/95), by installing equipment in such positions that live parts cannot be accidentally touched by hand or tools, while the protection degree of the cabinets and installation elements also prevents accidental contact.

- Protection against overloading is ensured by proper selection of thermal elements and automatic circuit breakers, in accordance with the Rulebook on Technical Normatives for Low-Voltage Electrical Installations (Official Gazette of SFRY No. 53/88, Official Gazette of FRY No. 28/95).

- Protection against unacceptable voltage drop is implemented in accordance with the Rulebook on Technical Normatives for Low-Voltage Electrical Installations (Official Gazette of SFRY No. 53/88, S…**

In accordance with the Rulebook on Technical Norms for Low-Voltage Electrical Installations (Official Gazette of the SFRY No. 53/88, Official Gazette of the FRY No. 28/95), the protection against impermissible voltage drop has been ensured by proper selection of conductor cross-sections, which has been verified by calculation.

- Protection against mechanical damage has been ensured in accordance with technical regulations, by selecting equipment suitable for the installation location.

- The influence of moisture, water, and dust has been addressed in accordance with the Rulebook on Technical Norms for Low-Voltage Electrical Installations (Official Gazette of the SFRY No. 53/88, Official Gazette of the FRY No. 28/95), through the use of installation devices with waterproof and dustproof protection, equipped with appropriate sealing.

### Occupational Safety

- Workers performing tasks under this project must be informed of all required measures they must apply for personal protection during work. The responsible departments within the working organization shall acquaint the workers with occupational safety measures. The application of these safety measures is the responsibility of both the work supervisor and the worker.

- Each worker must be provided with appropriate personal protective equipment and individual protective gear.

- Tools, devices, and other work equipment must be equipped with safety devices and the prescribed documentation confirming their suitability for safe operation. The execution of work tasks must be organized in such a manner that every worker can perform their duties without endangering their life and health, and without posing a risk to work equipment.

- A worker may only be assigned to tasks appropriate to their professional qualifications and health condition.

- The worker is obliged to report to their immediate supervisor any deficiency, incident, or suspicious occurrence that could lead to unwanted consequences for the worker, the work process, or the environment.

- The work supervisor and workers must be trained to provide first aid to any worker who may suffer an accident.

### Conclusion

The project has identified all potential hazards that may arise during the execution and operation of the investment facility and has defined all necessary measures for eliminating dangers and harmful effects in terms of occupational safety.

PROJECT OF TELECOMMUNICATION AND SIGNAL INSTALLATIONS

5.5. TEXTUAL DOCUMENTATION
5.5.1. Technical Description

The project refers to the construction of telecommunication connection lines for supplying the reconstructed towers 1 and 2.

The design of the telecommunication and signal installations includes the installation of cables from the multimedia boxes located in the towers to the RJ45 outlets.

This project also includes the construction of the telecommunication connection line for towers 1 and 2, running from the connection point on Kale Street to the multimedia boxes located in the towers.

The cables should be routed through PVC conduits placed under plaster in the joints between stones, and freely laid in trenches.

Structured Cabling System Installation
The structured cabling system consists of universal RJ45 outlets in the building, which are connected by cables to the outlets in the multimedia boxes. These connections are universal and can be used for connecting computers or telephones.

A connection must be established between the structured cabling system (SCS) multimedia boxes and the provider’s telecommunications service cabinet.

The distribution cabinets are connected to the outlets using U/FTP (4x2xAWF23) Cat 6a cables. This ensures a 10Gbase infrastructure that can be used over a long period, supporting multiple generations of active equipment.

The installation of all workstations is designed as structured cabling, meaning both telephone and computer networks are routed using U/FTP (4x2xAWF23) Cat 6a cables from the floor distribution points to individual RJ45 outlets. The RJ45 outlets are Category 6a, and the patch cables in the distribution cabinets are also Category 6a.

All cables—installation and patch—must be cables with enhanced fire-performance characteristics. They must possess a certificate of conformity with the SRPS EN 50525 standard and be tested in accordance with the SRPS EN 60332 standard.

Cables in the vertical distribution section are routed through halogen-free, self-extinguishing conduits of Ø32/26 mm. In the horizontal distribution section, cables are partially routed through halogen-free, self-extinguishing conduits of Ø20/15.5 mm in the wall under plaster, and partially on perforated cable trays.

Responsible Designer
Miodrag Penčić, B.Sc. Electrical Engineer

### 5.5.2. SPECIAL ANNEX ON OCCUPATIONAL SAFETY AND HEALTH

Special annex on the applied regulations, measures, and standards of occupational safety and health in the design of low- and high-voltage electrical installations, in accordance with the LAW ON OCCUPATIONAL SAFETY AND HEALTH (“Official Gazette of the Republic of Serbia”, No. 101/2005).

#### Hazards and harmful effects that may occur during the use of low- and high-voltage electrical installations

- Hazard of accidental contact with live parts

- Hazard of overload

- Hazard of short-circuit current

- Hazard of electric shock

- Hazard of excessive touch voltage and step voltage

- Hazard of incorrect operation

- Hazard of fire

- Hazard of the influence of water, moisture and dust, explosive and flammable materials, and chemical effects

- Hazard of unacceptable voltage drop

- Hazard of accidental mechanical damage

- Hazard of earth-fault current

- Hazard of power outage

- Hazard of static electricity

- Hazard of electromagnetic field exposure

- Hazard of radioactive radiation

- Hazard of lightning discharge

### Prescribed measures for eliminating hazards and harmful effects in low- and high-voltage electrical installations

#### Hazard of accidental contact with live parts

This hazard is eliminated by proper selection of electrical equipment.
The electrical equipment is designed for flush or surface mounting on walls and is equipped with protective enclosures and covers, preventing accidental contact with live components.
All power supply lines are of appropriate construction, equipped with adequate insulation and protective sheathing, and their proper introduction into connection cabinets and protective housings is ensured.

#### Hazard of overload

Overload protection is achieved by proper selection of protective circuit breakers and fuses on the central equipment side, preventing overload of all cables and devices.

#### Hazard of short-circuit current

This hazard is eliminated through proper dimensioning of cables and equipment for short-circuit conditions. Properly executed installation and assembly works, in accordance with manufacturers’ instructions, prevent the occurrence of short circuits.

#### Hazard of electric shock (indirect contact)

Protection against electric shock is provided by automatic disconnection in case of a fault (fuses) and by using low voltage (48 V).

#### Hazard of excessive touch voltage and step voltage

Protection is achieved by using a reduced-voltage system, correct equipment selection, grounding all metallic parts that do not belong to electrical circuits, and proper grounding electrode installation.
The hazard of step voltage is eliminated by constructing a common grounding system for the facility, connecting all metal masses inside and on the building.

#### Hazard of incorrect operation

By selecting equipment that meets standards and assigning trained personnel where required, the risk of improper operation is avoided.

#### Hazard of fire

Fire protection is ensured by proper selection of electrical equipment which, when installed and maintained according to regulations, cannot be a source of fire.

#### Hazard of water, moisture, dust, explosive and flammable materials, and chemical influences

Protection is achieved by selecting equipment appropriate for its purpose and installation location, taking into account operating conditions specified in the drawings and textual documentation.

#### Hazard of unacceptable voltage drop

Protection is ensured by properly dimensioning power supply lines.
Conductor cross-section calculations and voltage drop calculations are included in the project documentation.

#### Hazard of accidental mechanical damage

This hazard does not exist because all equipment is housed in metal enclosures, and all cables in locations at risk of mechanical damage are placed in protective conduits. Equipment is positioned so that it is not exposed to mechanical damage.

#### Hazard of earth-fault current

By constructing a common grounding system, the hazard of earth-fault current is eliminated.

#### Hazard of power outage

Protection from loss of mains voltage is ensured by installing batteries of sufficient capacity operating in parallel with rectifier units for normal supply.

#### Hazard of static electricity

This hazard is eliminated by proper grounding.

#### Hazard of electromagnetic field exposure

Protection is ensured by applying protective measures when routing cables in parallel with or crossing power lines, as well as grounding cable armouring at both ends.

### General notes and obligations

- An employer performing construction or reconstruction of a building, or changing a technological process for longer than seven days, must prepare the prescribed site organization study and submit it with the work commencement report to the competent labor inspection authority.

- The manufacturer of mechanized work equipment must provide instructions for safe operation and confirm that the prescribed occupational safety measures and standards have been applied.

- The employer must notify the competent labor inspection authority at least 8 days before starting work, and also when technological changes affect working conditions.

- The employer must, through a general act or collective agreement, define rights, obligations, and responsibilities in the field of occupational safety and health.

- The employer must prepare a written risk assessment for all workplaces and define methods and measures for eliminating risks.

- The employer must designate, in writing, a person responsible for occupational safety and health; train employees for safe work; provide personal protective equipment; inform employees of all risks associated with their tasks; and provide both theoretical and practical training.

- Periodic assessments of employee competence for safe work, for workplaces with increased risk, are performed as prescribed in the risk assessment document.

- Employers handling explosive mixtures must have a Rulebook on handling explosion-protected electrical installations and on keeping records of construction, repair, and maintenance of such installations. This Rulebook must also prescribe periodic inspections, which must occur at intervals not exceeding one year.

- The employer may provide employees with work equipment, personal protective equipment, or hazardous materials only if the required Serbian-language documentation for use, maintenance, packaging, transport, handling, and storage is available, including safety-technical information necessary for assessing and eliminating risks.

- When procuring work tools or devices, documentation must include information on acoustic characteristics to verify that noise levels will not exceed allowed limits. If special measures (e.g., silencers, elastic mountings) are required to meet noise limits, they must be specified.

- All equipment and materials specified in this project must comply with applicable Serbian technical regulations and standards.

- All installations and their maintenance must comply with current regulations.

- Wherever required by regulations, clearly visible warning signs must be installed indicating:

  - Voltage level

  - Purpose of specific equipment

  - Other important information

During installation or maintenance of equipment and systems, warning signs must indicate:

- On/Off status

- Restrictions

- Other important information for the operator

The use of protective equipment and means is mandatory when handling and operating within the facility.

### 5.5.3. TECHNICAL CONDITIONS

### General and Contractuel Conditions

- These technical conditions are an integral part of the project and are mandatory for the Contractor and the Investor.

- Before commencing work, the Contractor must familiarize himself with the project and request any necessary clarifications from the supervisory authority in due time.

- The Investor must entrust the execution of works to an authorized organization and appoint a supervisor who holds authorization for performing supervision.

- For all possible changes to the project design and any deviations—whether in terms of technical solutions or choice of materials—written approval from the Investor or his supervisory authority must be obtained. If the Contractor fails to do so, he bears responsibility for all changes and the works executed based on them.

- The Contractor must keep a separate work diary for the works covered by this project. Any unplanned works, increased quantities of materials, or modifications must be approved in advance by the Investor or his supervisory authority and must be entered into the work diary, verified by the supervisory authority or the Investor.

- During execution, care must be taken not to damage already completed structures or installations. Reinforced-concrete structures may be drilled only with written approval from the construction supervisory authority.

- Contractors (if more than one is engaged) must coordinate their work in terms of timing, space, and technical execution.

- The Contractor guarantees the correctness of the executed works for two years from the date of technical acceptance of the facility. Any defect occurring during operation due to poor-quality materials or faulty workmanship must be remedied by the Contractor without any right to compensation.

- All materials to be installed must meet standards and be of first-class quality. Materials not meeting these requirements must not be installed.

### Conditions for Work, Materials, and Equipment Layout

All materials used in this installation must be of first-class quality and manufactured according to SRPS standards.
All equipment is supplied complete for installation and operation unless otherwise specified.

During installation, the Contractor must ensure no previously completed works are damaged. If damage occurs through negligence or unprofessional conduct during electrical installation works, the electrical installation contractor bears full responsibility for the damage.

Demolition or cutting of columns, walls, or beams is not allowed without approval from the construction supervisory authority.

When placing cables or conductors in conduits, all conductors belonging to the same circuit must be placed in the same conduit or cable. Splicing of conductors may only be performed in junction boxes, distribution boxes, cabinets, and battery enclosures. Metal sheaths of conduits and cables may not be used as return conductors or grounding conductors.

Installation conduits and cables must be laid in straight vertical or horizontal lines. Curved routing is allowed only exceptionally. Horizontal conduits must have a slight slope toward boxes or shafts. Insulating bushings must be installed on the open ends of conduits.

Conduits and cables embedded in walls or floors must not be covered with materials that could corrode them. Conductors in conduits must be capable of being pulled through without difficulty, except in special cases.

Only waterproof equipment may be installed in damp rooms.

Cables are fixed to walls using clamps at the following intervals:

- 30 cm for 1.5 mm² conductors

- 40 cm for 2.5–4 mm² conductors

- 50 cm for conductors larger than 6 mm²

When passing through partition walls, conduits between wet and dry rooms must be installed so that moisture cannot enter or accumulate. Conduits must be made of moisture-resistant materials and placed with a slope toward the wet room. When laying conduits through the external walls of the building, the interior is considered a dry space relative to the exterior.

All equipment and installations must be mounted at the locations indicated on the drawings.

When installing parallel horizontal routes for low- and high-voltage lines:

- telecommunication cables are placed at the top of the wall,

- 10 cm below them are signaling lines,

- 10 cm below the signaling lines are power cables.

Distribution boxes in these routes are installed diagonally one below another at a 45° angle. At right-angle crossings, the distance between routes must be at least 10 mm. If this is not feasible, a 3 mm insulating insert must be installed.

Parallel routing next to chimneys or heating pipes should be avoided. If unavoidable, a minimum distance of 5 cm must be maintained. When crossing such structures, a minimum distance of 3 cm must be ensured, and electrical cables must be thermally insulated.

### Conditions for Low-Voltage Installation

- Installations must be carried out according to the written and graphical parts of the project and applicable Technical Regulations.

- Before and after laying cables, continuity of conductors, resistance, and insulation resistance must be checked. If insulation resistance does not meet requirements, cables must be replaced. Measurements must be performed with instruments rated for the nominal installation voltage but not less than 100 V.

- As plastic-insulated cables are used, attention must be paid to installation temperature. Cable laying must not be performed below +5°C. If installation is necessary at lower temperatures, the cable must be preheated before unwinding and pulling.

- During cable handling and pulling, procedures minimizing stress and preventing damage must be followed.

- Bending radius for PP-type copper cables must be at least 12–15 times the cable diameter.

- Minimum vertical clearance when crossing pipes:

  - 50 cm for 10 kV cables

  - 30 cm for 1 kV cables

- Parallel routing near building foundations or walls must maintain at least 50 cm distance.

- Cables in trenches must be marked with lead tags showing type, cross-section, and voltage. Tags must be placed every 5 m and at all entry/exit points of ducts and crossings.

- Cable lengths specified in the BOQ are approximate; actual lengths must be measured on site before cutting. Use longest possible cable segments with a minimum number of splices.

- Cables placed in floors, walls, or along structures must be routed through protective conduits; conduits must be pre-bent before inserting cables.

- Minimum distances between low-voltage and telecommunication cables:

  - 20 cm parallel

  - 10 mm at crossings

- Distribution cabinets must be manufactured according to the technical description. Cable entries must have appropriate glands.

- Cabinets must be connected to the building grounding system with galvanized steel strips.

- All materials and equipment must comply with current SRPS standards.

- After completion, all electrical and mechanical connections, grounding, and touch voltage must be tested, followed by test operation without load.

- Light switches must be installed on the side of the door that opens, at a height of 1.5 m. Socket outlets in residential areas must be installed at 30 cm from the floor; in other rooms, between 50 and 170 cm depending on requirements.

- Electricity meters must be placed at heights between 60 and 220 cm. Other distribution boards must be installed according to project requirements.

- The installation must be inspected and tested before handover, in accordance with regulations. Tests include:

  - continuity of protective conductors,

  - insulation resistance,

  - protective separation,

  - floor and wall resistance,

  - automatic disconnection of supply,

  - equipotential bonding,

  - functionality.

Continuity of protective conductors is tested using 4–24 V DC or AC with a minimum current of 0.2 A.

### Technical Conditions for Telecommunication and Signal Installations

a) Install all devices according to layout drawings. Any modifications require written approval from the supervisory authority. Before starting work, the Contractor must mark installation points for devices, cabinets, boxes, and conduits.
b) Details of device mounting on walls or supports are defined by the equipment manufacturer’s documentation.
c) Telephone installation must use PVC-insulated copper telephone cables with conductor diameter 0.6 mm.
d) All conduits and junction boxes for cables must be made of insulating material. The inner diameter must correspond to cable size and quantity. Conduits must be laid beneath wall finishing layers. Cables are pulled after wall finishing.
e) At directional changes, gentle bends with radius at least 15× cable diameter must be used.
f) Conduits between junction boxes must not have points where condensed water can accumulate.
g) Horizontal conduits must have a slight upward arch toward the center, with ends sloping toward junction boxes.
h) TK and EE cables laid in parallel must maintain at least:

- 20 cm separation (general),

- 30 cm below ceiling for EE cables,

- 10 cm above them for signaling,

- 10 cm above signaling for telephone cables.
For rigid conduits, minimum spacing between systems is 5 cm.
i) Crossings between TK and EE cables must be avoided. If unavoidable, crossings must be at right angles with minimum 10 mm separation. If not feasible, a 3 mm insulating insert must be installed.
j) All metallic parts of telecommunication devices, cabinets, distribution frames, and cable racks must be grounded with a stranded copper conductor connected to the building grounding system.
k) At device connection points, leave sufficient cable length for proper positioning. Desk telephone outlets must be placed 0.3 m above the floor. All cabinets must be mounted at 1.5 m height.
l) Cable routing beneath plumbing or sewage pipes is not allowed.
m) Where cables pass through floors, walls, or metal structures, protective PVC conduits of appropriate diameter must be installed. After cable pulling, conduits must be sealed with insulation compound. Protective conduits must be mechanically strong and nonflammable.
n) All metallic parts of telecommunication devices, cabinets, distribution frames, and racks must be grounded using a stranded copper conductor.
o) Cable installation temperature must not be below +5°C.

Responsible Designer:
Miodrag Penčić, B.Sc. Electrical Engineer

### 5.5.4. TECHNICAL REQUIREMENTS FOR PRODUCTS AND CONFORMITY ASSESSMENT

The technical requirements for products and conformity assessment are defined by the Law on Technical Requirements for Products and Conformity Assessment (“Official Gazette of the Republic of Serbia”, No. 36/2009). This law regulates the method of prescribing technical requirements for products and adopting technical regulations, assessing product conformity with prescribed technical requirements, the obligations of product suppliers and product owners during use, the validity of foreign conformity documents and conformity marks, notification on technical regulations and conformity assessment procedures, and supervision over the implementation of this procedure.

A product may be placed on the market or supplied on the market only if it is compliant with the prescribed technical requirements, if its conformity has been assessed according to the prescribed procedure, if it is marked in accordance with the regulations, and if it is accompanied by the prescribed conformity documents and other required documentation.

A technical regulation is any regulation that defines, for an individual product or group of products (hereinafter: product), at least one of the following elements:

- technical requirements the product must meet before being supplied;

- conformity assessment procedures;

- safety requirements during the product’s service life;

- regular and extraordinary inspections during the product’s service life;

- documents that accompany the product when placed on the market or into use;

- conformity marks and methods of marking products;

- requirements that must be met by conformity assessment bodies;

- packaging and labeling requirements.

Technical regulations and the technical requirements contained within them are adopted for the purpose of protecting safety, life and health of people, protection of animals and plants, protection of the environment, protection of consumers and other users, and protection of property.

The manufacturer places the conformity mark on a product that complies with the technical regulation, if prescribed by the regulation.

The Ministry maintains the following registers as public records:

- the register of valid technical regulations and designated or authorized conformity assessment bodies;

- the register of technical regulations under preparation;

- the register of foreign conformity documents and marks valid in the Republic of Serbia.

A distributor of a product is obligated to verify whether the required conformity mark is placed on the product and whether it is accompanied by the required documentation. If there is a justified suspicion that the product is not compliant with the prescribed requirements, the distributor may place the product on the market only after the manufacturer brings the product into conformity with those requirements, and must notify the manufacturer or importer and the competent authorities if the product is unsafe.

All designed materials in the facility, as well as materials that serve a specific function in case of fire and have a required level of fire resistance, must be accompanied by appropriate certification documentation compliant with this law.

Responsible Designer:
Miodrag Penčić, B.Sc. Electrical Engineer

## PROJECT OF MECHANICAL INSTALLATIONS

## 6.5.2. TECHNICAL DESCRIPTION

For the needs of the investor, the City of Pirot, Srpskih Vladara St. 82, Pirot, investment–technical documentation has been prepared – the Detailed Design (PZI) for the construction of the Partition Wall and Towers within the Pirot Fortress “Kale” in Pirot.

The project includes:

- VRF heating and cooling installation for Tower 1 and Tower 2

During the development of the investment–technical documentation for the mechanical installations, all relevant regulations, standards, SRPS and EN norms for this type of installation were taken into account. The documentation includes all necessary textual and graphical attachments.

### INTRODUCTORY SECTION

The heat-loss calculation for the heated rooms was carried out in accordance with the Rules for Calculating Required Heating Output for Buildings and the SRPS EN12831 standard. The design outdoor temperature adopted in the calculation is tsp = –15.8°C, in accordance with the Energy Efficiency Regulation.
The cooling load calculation was performed in accordance with the VDI 2078 standard.

When selecting heating units and equipment, special consideration was given to the specific characteristics of the local climate and previous experience in designing and operating this type of installation.
Room temperatures were adopted based on the technical conditions and standards prescribed for this type of facility and are provided in the graphical documentation and calculation files.

### NOTE:

During the adoption of the design solution, it was taken into account that the facility is a Serbian medieval fortification, categorized as a cultural monument of great importance and protected by the state.
This project was developed on the basis of the architectural–geodetic reconstruction project for Tower 1 and Tower 2, respecting all conservation and restoration works planned for the complete defensive wall of the fortress.

## 1. TOWER 2 – Café with Gallery (Ground floor + 1st floor)

### 1.1. VRF HEATING AND COOLING SYSTEM – TOWER 2

For heating and cooling the ground floor and the first floor, a VRF (Variable Refrigerant Flow) system has been designed.

The project provides the installation of a VRF Vitoclima 333-S Mini system by the renowned manufacturer Viessmann, Germany.

The following units have been specified:

### 1. Viessmann Vitoclima 333-S – Mini Outdoor Unit

- Full D.C. inverter compressors with direct expansion

- Model: EU-OV3160M1 (Cooling/Heating output = 16/18 kW) – 1 unit

- Operating temperature range:

  - Heating: –20°C to +24°C

  - Cooling: –5°C to +50°C

- Refrigerant: R410A

- Power supply: 1-phase, 220–240V, 50/60 Hz

- Connections: Ø19.05 / Ø9.52 mm

- Dimensions (WxDxH): 930 × 765 × 1605 mm

### 2. VRF Indoor Wall-Mounted Unit – Ground Floor Café

- Viessmann model: WV3022M2 – 2 units

- Output (Cooling/Heating): 2.2/2.5 kW

- Sound pressure level: 35/33/30 dB(A)

- Refrigerant: R410A

- Power supply: 1-phase, 220–240V, 50/60 Hz

- Electrical power: 35 W

- Connections: Ø9.52 / Ø6.35 mm

- Net weight (unit): 10.5 kg

- Net weight (panel): 3.5 kg

- Dimensions: 845 × 209 × 289 mm

### 3. Viessmann Vitoclima 333-VRF Indoor Unit – First Floor Café Gallery

- Floor-mounted console type – 2 units

- Model: FCV3036M1 (Cooling/Heating output = 3.6/4.0 kW)

- Sound pressure level: 32–36 dB(A)

- Refrigerant: R410A

- Power supply: 1-phase, 220–240V, 50/60 Hz

- Electrical power: 40 W

- Connections: Ø12.7 / Ø6.35 mm

- Net weight: 49 kg

- Dimensions: 1220 × 700 × 225 mm

For the ground floor café, considering the architectural–geodetic design and the available mounting space, two wall-mounted indoor VRF units are planned to be installed below the ceiling, in accordance with the manufacturer’s installation requirements. The installation locations are shown in the graphical documentation.

For the first-floor gallery of Tower 2, floor-mounted indoor units have been selected, adapted to the window parapet heights.

The selection of indoor units was made based on the calculations of winter heat losses and summer heat gains, adopting indoor design temperatures of min. 20°C (winter) and max. 26°C (summer), which comply with the regulations for this type of space.

The indoor units are controlled via a wired controller, model VWRCXK46.

The copper piping for liquid and gas refrigerant phases, sized for the appropriate capacity and freon flow, as well as the PPR condensate drainage network, is routed below the ground-floor ceiling and then through the space between the newly designed aluminum glazing and steel sheet panels mounted on a secondary steel substructure.
All piping is insulated with tubular insulation featuring a vapor barrier.

A concrete base and steel substructure are planned for the outdoor unit.

The final installation location of the outdoor unit, as well as the method of its visual screening—due to strict requirements of the fortress complex revitalization—will be determined on site, together with the investor’s representatives, while complying with the installation conditions prescribed by the manufacturer to ensure efficient and safe system operation.

The bill of quantities also includes the manufacture and installation of an electrical cabinet with all necessary components for supplying power to both indoor and outdoor units.

### 1.2. MECHANICAL VENTILATION – TOWER 2

For the required mechanical ventilation of the café (a physically unified space: ground floor + first floor), the installation of two window-mounted fans is planned.
Material: reinforced ABS plastic; integrated shutters; motor 230V–50Hz, class B, IPX4, insulation class II, with thermal protection via fuse.

Fan specifications:

- Type: HCM-225, Manufacturer: S&P

- 1700 rpm, 40 W, 900 m³/h, 49.1 dB, Ø 298 mm.

The fans are operated individually as needed, ensuring 5–8 air changes per hour, in accordance with recommendations for this type of space.

They are installed at the top of the window portals on the first floor (as shown in the graphical documentation). Air exhaust is directed into the gap between the façade screen and the portal.

## 2. TOWER 1 – Souvenir Shop with Exhibition Area (Ground floor + 1st floor)

Considering the structural rehabilitation performed on the building, its construction characteristics, and its size (net area: ground floor 11 m² + first floor 11 m² = 22 m² total), local standalone portable air-conditioning units of appropriate capacity are planned—one for each floor.
These units ensure the prescribed indoor temperatures of min. 20°C (winter) and max. 26°C (summer), in accordance with regulations for this type of space.

In all other aspects, this project was developed in accordance with applicable regulations, standards, and recommendations for this type of installation.
All remaining information is provided in the textual and graphical parts of this project documentation.

Responsible Designer:
Radomir Mančić, B.Sc. Mechanical Engineer

## 6.5.3. GENERAL CONDITIONS FOR CONTRACTING AND EXECUTION OF WORKS

- The assignment of construction of the subject investment facility shall be carried out in accordance with the applicable Law on Construction of Facilities.

- The contract for the execution of the planned works shall be concluded between the Investor and the Contractor, based on this approved project. The project represents an integral part of the contract between the Investor and the Contractor.

- This project serves as the basis for submitting bids and concluding the contract. All bidders must receive the project for review, as well as a typed bill of quantities without prices, into which they will enter their prices. All copies of the bill of quantities provided to bidders must be identical so all bidders will offer the same works, in the same quantities, and of the same quality.

- The offer must include prices for: all required materials of appropriate quality; customs and other import expenses for imported equipment; all material transport, both external and within the construction site; all travel and transportation expenses for the workforce; complete execution of installation works including preparatory and finishing works. In other words, the offer must include all costs up to the final technical inspection and approval by the competent commission.

- The Investor shall award the works to the most favorable bidder. The Investor evaluates the favorability of the offer not only by price, but also by the bidder’s business reputation, technical capacity, and legal eligibility for executing the works.

- The construction contract is considered concluded once the parties agree in writing on the construction of the facility and the construction price.

- The execution contract must also include:

  - deadlines for the start and completion of all works;

  - method of payment for completed works;

  - penalty provisions;

  - warranty period with specification of exclusions;

  - supervision over the execution of works;

  - the contractor’s obligation to perform works according to the approved project and in accordance with applicable regulations, standards, technical instructions, and norms.

- The contract must designate the individual legally authorized to manage the works on-site. Likewise, the contract must designate the individual who will represent the supervision on-site and perform supervision for all works, in accordance with legal requirements.

- Installations and equipment must be executed so that they fully comply with the project, manufacturer requirements, and applicable regulations and standards. Any deviation from the project is allowed only with prior approval from the designer, and all changes must be recorded in the construction logbook.

- Execution of the facility must not begin without a building permit issued by the competent authorities. The Investor must provide the Contractor with electricity and water prior to the start of works.

- The Contractor must timely warn the Investor about all preparatory works needed before other contractors start their work so that deadlines for completing these preparatory works can be agreed upon.

- Before beginning the works, the Contractor must visit the site, verify the project, and compare it with the actual conditions or with the construction project if the building is not yet completed. If discrepancies are found, the Contractor must request project adjustments with proper justification.

- The Contractor must:

- execute works according to the project;

- execute works according to regulations, standards, technical norms, and quality norms applicable to this type of facility;

- undertake timely measures for the safety of the facility, works, equipment, workers, passers-by, traffic, and neighboring structures;

- implement environmental protection measures;

- coordinate the organization of works with other contractors to minimize disruptions.

- The warranty period for installation works shall follow legal regulations unless otherwise agreed in the contract. Manufacturer warranties apply to installed equipment. The warranty period begins from the date of technical acceptance of the works, provided the commission issues a positive report. If acceptance is delayed due to the manufacturer, the warranty begins from the date acceptance should have occurred.

- Any defect occurring during the warranty period due to poor-quality material or improper workmanship must be repaired by the Contractor at their own expense upon first request. If the Contractor does not respond, the Investor may engage another contractor, with the costs charged entirely to the original Contractor.

- Damage caused by force majeure shall be repaired by the Contractor at their own expense, but the Contractor is entitled to an extension of the completion deadline. Days of severe weather are excluded from working days and must be recorded in the construction logbook.

- All materials used must be new, of good quality, free of factory defects, and compliant with applicable regulations and Serbian standards. Installed material must be accompanied by valid certificates. The Contractor is fully responsible for defective materials and must cover all costs of replacement.

- If the supervisory authority requests testing of any material, the Contractor must submit it for testing to an authorized institution. If the material is compliant, testing costs are charged as additional work, and the Contractor is entitled to a deadline extension. If the material is non-compliant, it must be removed at the Contractor’s expense.

- If the Investor supplies any materials, the Contractor must inspect them and reject faulty materials. If the Contractor determines that the Investor’s material is not compliant, they must refuse installation and record this in the construction logbook. If the supervisory authority insists on installation of unsuitable material, the Contractor must install it but is not responsible for its performance, which must be documented in writing.

- If the Contractor executes installation works fully according to the project and with the prescribed material, they are responsible only for the workmanship and the performance of installed components. Unauthorized changes to the project are strictly prohibited. Minor changes may be approved by the competent authority, while major changes require project revision by the designer and re-approval by the Investor.

- If the Contractor identifies technically incorrect, unsafe, or uncoordinated solutions, they must immediately notify the Investor and request changes. Failure to do so makes the Contractor liable for resulting damages.

- If additional works or project modifications are required that were not included in the contract, the Contractor must submit a cost estimate to the Investor. Additional works may begin only after Investor approval. The Investor must respond within eight days; otherwise, the offer is considered rejected.

- The installation cost includes (unless otherwise specified in the contract): complete installation, testing, adjustments, trial operation, worker training after completion, and compensation for technicians and assistants.

- The Contractor must have qualified supervisory personnel on-site, as required by law. All workers must have appropriate qualifications. The supervisory authority may order removal of unqualified workers.

- Domestic equipment manufacturers must provide certificates from authorized institutions in accordance with the Law on Occupational Safety and Health.

- The Contractor must protect surrounding structures, avoid damage to the facility and existing installations, and repair or compensate for any damage caused intentionally or through negligence.

- All waste generated by the Contractor must be removed from the site at the Contractor’s expense.

- The Contractor must implement all safety measures for workers according to applicable regulations.

- Financial obligations between the Investor and Contractor are regulated by contract, including the payment method.

- During construction, the Contractor must maintain a construction logbook in accordance with regulations. All changes and deviations must be recorded. The logbook must be certified by the supervisory authority and the Contractor.

- In addition to the logbook, the supervisory authority keeps a construction book recording all completed works. This book forms the basis for payment and long-term documentation.

- The facility must not be used before technical inspection is conducted. Inspection is performed based on a request from either the Contractor or Investor.

- The Contractor must prepare and submit an operating manual for the installation in three copies, one of which must be framed and accessible on-site.

- The Contractor must prepare as-built project documentation in three copies and deliver it to the Investor.

- If the Contractor determines that works cannot be completed on time, they must request a deadline extension at least ten days before the contractual deadline expires.

- If fewer works are executed than specified, the Contractor is entitled to compensation, which must be defined in the contract.

- The Investor must ensure a qualified supervisory person during construction, in accordance with legal requirements.

- A contract is concluded with the supervisory person, defining their authority to approve additional works.

- The contract must specify compensation for the Investor in case of supervisory negligence.

- The Contractor is responsible only to the supervisory authority, and communication occurs through the construction logbook.

- After installation works are completed, the entire system must be tested with the supervision present.

- Test reports must include:

- subject of testing;

- list of persons who performed and attended the testing;

- date and time;

- environmental conditions;

- test results with exact values;

- conclusion on compliance;

- signatures of all involved persons.

- Works are considered completed when the Contractor submits a written report to the supervisory authority and the authority confirms it in writing.

- Before submitting a request for technical inspection and usage permit, the Investor must arrange an internal technical inspection.

- Fifteen days before completion, the Investor and Contractor submit a request for formation of a technical inspection commission.

- Technical inspection must begin within fifteen days after the request is received.

- For technical inspection, the Contractor or Investor must prepare the following documentation:

- building permit with approvals;

- complete technical documentation with all revisions;

- safety and fire protection assessments;

- certificates for installed materials;

- reports on structural control;

- test reports and results;

- welder certificates;

- logbooks;

- internal inspection report;

- operating and maintenance manuals with system diagrams.

- The commission must review all documentation and works, then issue its opinion. All inspection costs are borne by the Investor.

- After obtaining a usage permit, the facility may enter trial operation.

- If commissioning occurs after the contractual deadline, an internal commission must re-examine the facility.

- After obtaining the usage permit, the Investor and Contractor must carry out final handover and accounting within the legal deadline.

- The Contractor must provide measuring instruments and necessary manpower for technical inspection.

- The Contractor must immediately correct, at their expense, all defects identified during technical inspection.

- If changes or additional works beyond the contract scope are required, their costs are borne by the Investor.

- Such works must be performed by the Contractor.

# 6.5.4. TECHNICAL CONDITIONS FOR THE EXECUTION OF WORKS

## Technical Requirements for General Piping Installations

### a) General Section

- The installation must be executed fully in accordance with the project and may be entrusted only to a contractor who can guarantee and prove the ability to deliver, install, test, and commission the entire installation.

- Before the start of works, the contractor is obliged to review the project, compare it with the actual site conditions, and notify the investor of any potential project deficiencies or significant necessary changes, requesting further instructions.

- The installation contractor declares that they possess the knowledge and capability required for installations of this type, namely:
a) the ability to procure, deliver, install, connect with other system components, regulate, and commission all installation elements specified in the project, whether of domestic or imported production, including obtaining all necessary brochures, manuals, and technical documentation;
b) the knowledge and capability to resolve all installation details, both technically and aesthetically, where no detailed drawings have been provided—such as pipe hangers, fabrication of fixed and sliding supports, installation of air vents, mounting equipment on floating, elastic, or fixed foundations, and integrating equipment within the architectural-civil design;
c) the ability to regulate operating parameters of the installation—flow velocity, flow rate, and water temperature—using all regulation elements specified in the project.

- Installation components that are not serially manufactured but custom-made must be produced from quality materials and fabricated using the best methods applicable for that type of work. Surface protection must be carried out exactly as specified in the project, or if unspecified, in the standard manner for that type of work and in accordance with quality regulations.

- Before work begins, the contractor and investor must designate areas on-site for storage of equipment and materials required for assembly, as well as space for contractors. Only after this may equipment, materials, tools, and other items be delivered to the site.

- Transport of pipes:
a) Transport of pipes and all other pipeline components to the site or warehouse is carried out by truck. Access roads must be suitable for heavy vehicles and trucks with loading platforms 12–16 m long.
b) To protect the pipe interior, factory-installed end caps must remain on the pipe ends until installation. These caps must not be removed, even during handling or unloading. Pipes must be evenly supported along their length.
c) The truck loading platform must be checked for protruding or sharp objects. If present, they must be removed to prevent pipe damage, especially to the PEHD plastic jacket.
d) All couplings, sealing materials, end caps, gaskets, etc., must be delivered in protective packaging, which must not be removed until installation.

- Unloading from trucks:
a) Unloading must be performed by the pipe installation contractor or an authorized third party, ensuring compliance with all safety regulations. Pipes and components must not be dropped from the truck.
b) Smaller pipes and components may be unloaded manually. Larger pipes require cranes. For 12–16 m long pipes, two textile/nylon slings (10–15 cm wide) must be used, and the spreader bar must be at least 4 m long.
c) This prevents excessive pipe bending and potential damage to integrated systems such as surveillance wires.

- Storage of pipes:
a) Pipes must be stored on level, dry ground, free of stones, preferably sorted by size. Storage on ground exposed to groundwater or standing water is prohibited. Sand or wooden beams may be used as base support. Beams should be 10–25 cm wide, spaced 2 m apart, and surface pressure must not exceed 40 N/cm².
b) Storage height must not exceed 2.5 m. Pipes may be stacked in trapezoid or rectangular formations and must be secured against lateral sliding using supports, braces, or wooden wedges.
c) For long-term storage, appropriate protection from weather must be applied. During freezing temperatures, pipes and accessories must be additionally protected from bending, pressure, and impact.
d) Fittings, couplings, end caps, and expansion pillows must be stored dry, sorted, frost-protected, and out of direct sunlight. PUR foam components must be stored in lockable rooms/containers at +15°C to +25°C. Frozen (crystallized) PUR foam must not be used.

- During installation, a trial assembly of the installation components is recommended in the contractor’s workshop, with final assembly on-site.

- Electrical installations must use appropriate conductors and waterproof components, based on a dedicated electrical project derived from this project’s data.

- The contractor must obtain detailed wiring diagrams, installation instructions, and operating manuals from the automation supplier. If possible, the supply price should include the cost of a qualified representative to supervise assembly and commissioning of automation equipment.

- Electrical control cabinets must include all required switches and fuses. Each motor must have an indicator lamp, and voltage and current meters must be installed. All required relays and automation devices must be mounted on the control panel. The contractor must provide all materials for wiring motors and other electrical devices.

b) Pipeline

- The pipeline must be made of new, first-class material.

- Pipe shape and dimensions must conform to SRPS C.B5.026. Permissible deviations in pipe outer diameter and wall thickness must conform to SRPS EN 10220:2005. Pipes must be delivered in standard lengths with manufacturer certificates.

- Pipe elbows must have wall thicknesses corresponding to the specified standards.

- The pipeline is installed underground, in a trench.

- Steel pipelines must be joined by welding. Flanged connections may be used only for removable components (e.g., shut-off valves, strainers) with suitable gaskets.

- Pipeline layout must follow the project to enable thermal expansion without damage. Supports embedded in walls must use cement mortar—gypsum is prohibited. Drilling structural elements requires supervision approval.

- Pipes must be placed on temporary supports (wood, styrofoam, sandbags) or a 10 cm sand bed. Sufficient working space must be provided at joints. Supports must be placed every 2 m.

- Wooden supports must be removed before backfilling. Sandbags must be cut before refilling.

- Foundations must be leveled to ensure correct alignment without undesired stress.

- Installation in developed urban areas requires consideration of existing utilities. Drawings and documentation must be reviewed before work begins.

- The pipeline must not be used for grounding electrical equipment.

### c) Valves and Fittings

- Valves must comply with pipeline operating requirements and must have certificates. Each valve must be marked with nominal diameter, pressure rating, and flow direction.

- Shut-off valves must be supplied with flanges, counterflanges, gaskets, and bolts appropriate to the pressure class, and must be corrosion protected.

- Selection of valves must aim to minimize leakage and pressure loss.

### d) Supports and Hangers

- Support and hanger materials must ensure safe, continuous, and unobstructed support and guidance of pipes at operating temperatures and loads.

- All support elements must be coated twice with corrosion-resistant paint suitable for operating temperature.

- Sliding supports must be installed according to pipeline design requirements, ensuring the pipe rests on movable supports without pre-stressing.

### e) Insulation

- Hot water distribution pipes in the boiler room must be insulated with mineral wool covered with 0.55 mm aluminum sheet.

- Insulation must retain permanent structure and mechanical properties at operating temperatures.

- Valves must also be insulated using methods prescribed by the manufacturer.

### f) Expansion Elements

- Thermal expansion is compensated by natural compensation (‘L-type’ compensators) through proper route design.

g) Welding

Before starting pipe or pipeline section welding, the joints must be wetted with appropriate clamping (sealing) sleeves on the pipe cladding to be welded (at the welding site). If adverse weather conditions prevail, a protective tent should be erected above the connection site. During welding, the outer surfaces of the pipe's thermal insulation should be protected from burning using wet cloths or reflective blankets attached to the pipe.

Surfaces to be welded must be completely degreased and cleaned to a metallic luster from all traces of paint, rust, and other impurities. Internal cleaning should be performed with a cleaner consisting of two metal plates with a mounted steel brush or a piece of unraveled steel wire. The cleaner should be mounted on a sufficiently long steel rod, and manually threaded through the pipe in both directions until the pipe is clean. External cleaning should be done with steel brushes or scraping tools. Beveled pipe ends should be cleaned with a steel brush to a metallic shine. The use of tools that can damage the pipe surface (files, cutters, etc.) on beveled ends is not allowed.

Before welding, the pipe ends' measurements (tolerances) should be checked, and unsuitable pipes should be discarded or repaired. Minor damages caused during transport or handling should be repaired on-site before installation. Small dents should be straightened with a cold hammer, ensuring no damage to the pipe ends. Damaged beveled pipe ends should be corrected by making a new bevel using a gas cutting device that cuts and bevels simultaneously.

When pipes are aligned and flush with a 1.6 mm gap, an external coupling must be installed, and both pipes should be tightly clamped to prevent movement during welding.

For pipes with an outside diameter from ø17.2 to ø60.3 mm, welding is performed using gas-flame method, while for pipes over ø60.3 mm, manual electric welding is used.

Welding can be performed if the ambient temperature is above 0°C, and there is no wind or rain. For temperatures up to -50°C, preheating of the base material is necessary; welding should be halted at lower temperatures.

Welding should be performed in two layers: the root weld and the fill. Quality control of each joint must be continuously carried out, with all necessary data recorded in the welding log for any necessary correction of poorly executed welds.

Root welds should be made with electrodes ø3.25 mm, and fill layers with electrodes ø4 mm. The surface of the weld should be smooth and free of holes. The maximum excess weld height should not be more than 1.6 mm, nor less than 0.8 mm. The weld width must not exceed the width of the groove by more than 1.6 mm on both sides.

After the root weld, the weld must be ground down to the base material. During application of subsequent layers, the start and end of the weld should also be ground.

Pipe and flange welding must be performed so that the cross-section of the pipe at the weld seam does not change.

When welding flange connections, the mating surface of the flange must be perpendicular to the pipe axis. Deviations in parallelism of the mating surfaces should be within ±0.50 mm. Before welding, flange mating surfaces must be thoroughly cleaned of corrosion and dirt.

The distance between flanges must match the exact length of the pipe element. Tolerance for the distance should be within ±0.1 mm. Larger deviations can cause undesired consequences. Sealing material must be of good quality and uniform thickness; uneven thickness causes non-parallel sealing surfaces and additional stress.

Pipe welding must be performed with the following quality classes: minimum Class I, subclass IB. Only welders certified according to applicable regulations issued by the competent authority may perform this welding. Certification must not be older than six months.

Radiographic testing of all welded joints is mandatory at 100%. Depending on the results, the supervising authority may require increased or decreased testing scope.

h) Deaeration, sludge removal, and flushing of pipelines

Vent valves should be installed at the highest points of the pipeline according to the attached graphical documentation.

Sludge removal and drainage valves should be installed at the lowest points of the pipeline.

After completing the installation of pipelines, fittings, and discharge valves, the pipeline must be flushed with water.

After the initial flushing and removal of coarse dirt, pumps in the boiler room should be activated to circulate water through the pipeline system. During circulation, the system should be re-flushed, and part of the water should be discharged through the drain valves. After flushing, the entire volume of water should be drained.

Following water circulation, the pipeline should be filled with chemically softened water.

i) Final anticorrosive protection of pipelines, pipe supports, and steel brackets

Before applying the anticorrosive coating, all welds must be cleaned, slag removed, and other dirt and impurities cleaned from the entire outer surface using mechanical methods with cloth or other material and appropriate degreaser.

The final anticorrosive protection consists of applying two layers of coating with paint that must be durable and resistant to various temperatures. The warranty for this coating should be at least one and a half years, with a durability exceeding five years. Application should be done using a spray, brush, or roller.

The color of the final anticorrosive coating must differ from that of the primary anticorrosive protection if the main elements are supplied with the primary coating. Markings engraved on the pipeline are strictly prohibited.

The pipeline must be properly grounded. All flange joints must be bridged with a transition resistance of less than 0.03 Ω.

j) Testing of pipelines and fittings

The test pressure should be from 1.1 to 1.5 times the operational pressure for the specific installation, with the difference between test and operational pressure not less than 50 N/cm², according to SRPS EN 1333:2005 (SRPS M.B6.006).

If pipeline sections are at different elevations, the hydrostatic pressure during testing in each section should include the test pressure.

The duration of maintaining test pressure should not be less than 30 minutes. It should be long enough to reveal any critical weak points at joints and allow for inspection of all joints.

After inspections under test pressure, the pressure can be reduced to the nominal operating pressure for detailed system inspection.

Welded and other joints not previously factory-tested should not be painted, covered with earth, or insulated before successful strength testing.

Before testing, all pipelines interior must be cleaned of metal shavings, sand, rust, spent electrodes, and other foreign substances.

All elements of the pipeline, such as flanges, flow valves, shut-off valves, welded attachments for measurement and regulation instruments, supports, holders, sliders, rigid supports, and similar, must be finally installed before testing.

Equipment that should not be subjected to test pressure (such as pumps, inlet/outlet valves, and equipment without specified test pressure) must be disconnected with blind flanges before testing.

Manometers with measurement ranges smaller than the test pressure should be removed during testing.

Flow valves should be in the open position unless otherwise specified. Automatic regulation valves should always be open unless equipped with bypass lines.

The system must be equipped with openings for deaeration at all high points where air may accumulate. Drain outlets for depressurization should be at all low points and behind check valves.

The testing fluid (water) should be supplied at the lowest point of the system.

The test manometer must:

Be calibrated and certified;

Have a measurement range approximately twice the expected test pressure;

Be installed at the lowest point of the system and be accessible.

All joints being tested must be cleaned and dried before testing. Testing can only proceed when water temperature and equipment are at least 50°C.

After reaching the desired test pressure, the power source (pump) must be disconnected from the system.

Use clean water free of sludge and impurities for testing.

If leaks are observed at welded joints or base material, the system must be drained, repaired, and re-tested.

If leaks are detected at threaded joints, the system must be depressurized before repairs, then re-pressurized and tested again.

If pressure drops during test, causes must be identified (e.g., excessive water outflow or residual air). After fixing the cause, testing should be repeated.

After testing, no additional welding should be performed unless authorized, and re-testing is required if welding is done. Such welding must be closely monitored, performed at ambient temperatures above 13°C, and all welds must be 100% radiographically tested afterward.

Tightness testing of the installation should be performed immediately after strength testing. The test pressure should be equal to the operational pressure. The system is considered to withstand the tightness test if the pressure drops no more than 2% within 24 hours or other specified time.

A report must be prepared for each testing, signed by all members of the committee.

FIRE PROTECTION

## Division of the Building into Fire Compartments

Based on the purpose, contents, and use of the building, and in accordance with SRPS U.J1.240/94, point 2.2, the public buildings Tower I and Tower II represent separate fire segments, i.e., separate fire compartments.
The division into fire segments and fire compartments is carried out structurally by walls and ceilings of a defined fire resistance. Partition walls that serve as fire-resistant walls extend from one load-bearing structure to another, i.e., from floor to ceiling.
Main power supply cables in the building, as well as other electrical installations passing through fire-resistant walls or ceilings, shall be executed so that wall penetrations are properly sealed with non-combustible material after the installation passes through.
The division of the building into fire compartments is shown in the graphic annexes of the project.

No. | Fire Compartment | Area (m²)
PS1 | Tower I – exhibition display | 22.00
PS2 | Tower II – café/confectionery | 82.00

## Definition of Evacuation Routes

In the design of high-rise buildings, and in accordance with Article 40 of the Fire Protection Law, safe evacuation conditions must be planned and foreseen in case of fire.
Evacuation is the movement of persons from the starting point to a safe place in case of danger.
Evacuation routes must be visible, without unnecessary turns, with direction changes not exceeding 90° (except in staircases), and without horizontal and vertical obstacles that impede evacuation.
If there are lateral obstacles on evacuation routes (e.g., cabinets in hallways), the actual width of the obstacle is deducted from the actual floor width of the evacuation path.
The corridor width must not be less than 1.2 m, and the width of a staircase flight not less than 1 m. The required width of corridors and staircases depends on the number of people that need to evacuate.
Wall, ceiling, and floor coverings in communication areas belonging to the evacuation corridor must have a reaction-to-fire classification of at least A2-s1, d0 according to SRPS EN 13501-1.
Wall, ceiling, and floor coverings installed on evacuation routes not covered by the previous paragraph (e.g., floor-level hallways), depending on the evacuation stage, must have a reaction-to-fire classification of at least B-s1, d0 or B-fl-s1, according to SRPS EN 13501-1.

Evacuation routes must be illuminated with emergency lighting.
Emergency lighting — including lighting of direction signs, evacuation routes, and rooms larger than 60 m² (except dwellings) — must comply with SRPS EN 1838, SRPS EN 60598-2-22, and SRPS EN 50172.

Evacuation routes must be marked with signs indicating the direction of exit to a safe area, as well as emergency exits.
All signs must comply with SRPS ISO 7010.
Signs must be placed so as to be clear, unambiguous, and not pose danger themselves. Excessive clustering of signs should be avoided.
Signs must not be installed on movable objects or near movable objects that could block visibility when moved, except when required for safety.
When conditions change such that a sign becomes misleading or unnecessary, it must be removed.
Signs must be visible at night and in unfavorable conditions. Special attention must be given to visibility in emergencies (fire, power outage, smoke, etc.).
Signs must meet the colorimetric and photometric properties required by SRPS ISO 3864-4.

Evacuation plans and written instructions for fire-emergency procedures must be posted at eye level in the following locations:

- At all building entrances

- At access points to each floor

- At dead-end communication areas

- In every room used by a larger number of people

The evacuation plan must be prepared in accordance with ISO 23601.

Up to 8 persons may be present in Tower I and 57 persons in Tower II, with direct exit to open space.
The final finishing of horizontal and vertical surfaces of exits, exit paths, and evacuation paths defines the conditions for safe evacuation.

The total evacuation time from Tower I in the worst-case scenario is 34 seconds, which fully meets evacuation criteria.
Considering that the preparation time for evacuation in public buildings is 3 minutes, the maximum evacuation time for Tower I is 3 minutes and 34 seconds.

The total evacuation time from Tower II in the worst-case scenario is 63 seconds, which also fully meets evacuation criteria.
Thus, the maximum evacuation time for Tower II is 4 minutes and 2 seconds.

In 90% of cases, the evacuation time will be shorter due to varying numbers of occupants.

Based on these findings and calculated results, it is concluded that the number of evacuation exits is sufficient and that the evacuation time for this type of building is compliant.

## Selection of Materials for Fire-Resistant Structures

- For determining fire resistance for Tower I – Exhibition Space, the methodology prescribed by the Rulebook on Technical Standards for Fire Protection shall be used ("Official Gazette RS", No. 22/2019). The building is classified as a detached public building up to 8 m high (IJ1), with a fire compartment up to 400 m² accommodating up to 10 persons (P1).

- For determining fire resistance for Tower II – Café/Confectionery, the same methodology applies. The building is classified as a detached public building up to 8 m high (IJ1), with a fire compartment up to 400 m² accommodating up to 57 persons (P3).

For Towers I and II, within the fire compartment (SOP III):

- Load-bearing walls must have at least 60 minutes fire resistance (SRPS EN 1365-1).

- Non-load-bearing interior walls must have at least 30 minutes (SRPS EN 1364-1).

- Floor structures must have at least 30 minutes (SRPS EN 1365-2).

- Load-bearing columns must have at least 60 minutes (SRPS EN 1365-4).

- Load-bearing beams must have at least 30 minutes (SRPS EN 1365-3).

- Roof structure is not separated by a fire-resistant floor slab; therefore, it must meet SOP III requirements of 30 minutes.

- Evacuation route structure must provide 30 minutes resistance.

- Roof covering must also meet 30 minutes resistance requirements.

For both towers, steel structural elements must be protected with fire-resistant coatings corresponding to fire resistance requirements (SOP III):

- Load-bearing columns: 60 minutes

- Load-bearing beams: 30 minutes

- Steel staircase: 30 minutes

- Roof structure elements: 30 minutes

Protection of steel elements is defined by SRPS EN 13381-4, EN 13381-6, and EN 13381-8.
All steel elements shall be protected using appropriate certified intumescent coatings tested according to SRPS U.J1.042:2000 and SRPS U.J1.043:2000.

NOTICE related to all works specified in tender dossier  : “Should the technical description or any other part of the project documentation contain indications or references to a specific manufacturer, brand, or trademark of materials or products, the Tenderer  is free to propose an adequate and equivalent alternative from any other manufacturer. The project documentation does not favor any particular manufacturer of materials or equipment; such references are used solely for the purpose of defining the required items for the execution of works.”